## CompareList
NRC Comparisons
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
Experiment | FM_SNL_Test_4_Exp | 2
Model | FM_SNL_Test_4_Mod | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 3 | 1 | 2 | 0 | 15 | Max
Compare | HGL Height | HGL Height | 1 | 2 | 1 | 3 | 0 | 15 | Min | Closed |  | 6.1 |  |  | 6.1
Compare | Temperature 1/0.98H | Ceiling Jet Temperature | 5 | 6 | 1 | 9 | 0 | 15 | Max
Compare | Temperature 11/0.98H | Ceiling Jet Temperature | 5 | 16 | 1 | 8 | 0 | 15 | Max
Compare | Temperature 28/0.98H | Plume Temperature | 5 | 21 | 1 | 10 | 0 | 15 | Max
Experiment | FM_SNL_Test_5_Exp | 2
Model | FM_SNL_Test_5_Mod | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 3 | 1 | 2 | 0 | 15 | Max
Compare | HGL Height | HGL Height | 1 | 2 | 1 | 3 | 0 | 15 | Min | Closed |  | 6.1 |  |  | 6.1
Compare | Temperature 1/0.98H | Ceiling Jet Temperature | 5 | 6 | 1 | 9 | 0 | 15 | Max
Compare | Temperature 11/0.98H | Ceiling Jet Temperature | 5 | 16 | 1 | 8 | 0 | 15 | Max
Compare | Temperature 28/0.98H | Plume Temperature | 5 | 21 | 1 | 10 | 0 | 15 | Max
Experiment | FM_SNL_Test_21_Exp | 2
Model | FM_SNL_Test_21_Mod | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 3 | 1 | 2 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 2 | 1 | 3 | 0 | 30 | Min | Closed |  | 6.1 |  |  | 6.1
Compare | Temperature 1/0.98H | Ceiling Jet Temperature | 5 | 6 | 1 | 9 | 0 | 30 | Max
Compare | Temperature 11/0.98H | Ceiling Jet Temperature | 5 | 16 | 1 | 8 | 0 | 30 | Max
Compare | Temperature 6/0.98H | Plume Temperature | 5 | 11 | 1 | 10 | 0 | 30 | Max
Experiment | ICFMP2_Case_1 | 1
Model | ICFMP2_Case_1 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 83 | 34 | 35 | 0 | 8 | Max
Compare | HGL Height | HGL Height | 1 | 81 | 34 | 36 | 0 | 8 | Min | Closed |  | 19 |  |  | 19
Experiment | ICFMP2_Case_2 | 1
Model | ICFMP2_Case_2 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 4 | 6 | 7 | 0 | 8 | Max
Compare | HGL Height | HGL Height | 1 | 2 | 6 | 8 | 0 | 8 | Min | Closed |  | 19 |  |  | 19
Experiment | ICFMP2_Case_3 | 1
Model | ICFMP2_Case_3 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 46 | 35 | 36 | 0 | 8 | Max
Compare | HGL Height | HGL Height | 1 | 44 | 35 | 37 | 0 | 8 | Min |  |  | 19 |  |  | 19
Experiment | ICFMP3_Test_1 | 1
Model | ICFMP3_Test_1 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | [14 empty] | No experimental measurement
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | [14 empty] | No experimental measurement
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | [14 empty] | No experimental measurement
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max
Experiment | ICFMP3_Test_2 | 1
Model | ICFMP3_Test_2 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 342 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | [14 empty] | No experimental measurement
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 365 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max
Experiment | ICFMP3_Test_3 | 1
Model | ICFMP3_Test_3 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | [14 empty] | No experimental measurement
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max
Experiment | ICFMP3_Test_4 | 1
Model | ICFMP3_Test_4 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 342 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 354 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max
Experiment | ICFMP3_Test_5 | 1
Model | ICFMP3_Test_5 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 354 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | 0 | 30 | Max
Experiment | ICFMP3_Test_7 | 1
Model | ICFMP3_Test_7 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 342 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 365 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372
Experiment | ICFMP3_Test_8 | 1
Model | ICFMP3_Test_8 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 354 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max
Experiment | ICFMP3_Test_9 | 1
Model | ICFMP3_Test_9 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 139 | 325 | 346 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 166 | 325 | 348 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 17 | 325 | 369 | [14 empty] | No experimental measurement
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 31 | 325 | 371 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max
Experiment | ICFMP3_Test_10 | 1
Model | ICFMP3_Test_10 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372
Experiment | ICFMP3_Test_13 | 1
Model | ICFMP3_Test_13 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 139 | 325 | 346 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 177 | 325 | 351 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | [14 empty] | No experimental measurement
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | [14 empty] | No experimental measurement
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | [14 empty] | No experimental measurement
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 369 | [14 empty] | No experimental measurement
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | [14 empty] | No experimental measurement
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | [14 empty] | No experimental measurement
Compare | Ceiling 1 Flux | Surface Flux | 1 | 36 | 325 | 374 | [14 empty] | No experimental measurement
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | [14 empty] | No experimental measurement
Experiment | ICFMP3_Test_14 | 1
Model | ICFMP3_Test_14 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max | [11 empty] | No experimental measurement
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | 0 | 30 | Max
Experiment | ICFMP3_Test_15 | 1
Model | ICFMP3_Test_15 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 125 | 325 | 340 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 124 | 325 | 341 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | [14 empty] | No experimental measurement
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 8 | 325 | 363 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 10 | 325 | 364 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372
Experiment | ICFMP3_Test_16 | 1
Model | ICFMP3_Test_16 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 177 | 325 | 351 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | [14 empty] | No experimental measurement
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | [14 empty] | No experimental measurement
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | [14 empty] | No experimental measurement
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | [14 empty] | No experimental measurement
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | [14 empty] | No experimental measurement
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | [14 empty] | No experimental measurement
Compare | Ceiling 1 Flux | Surface Flux | 1 | 36 | 325 | 374 | [14 empty] | No experimental measurement
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | [14 empty] | No experimental measurement
Experiment | ICFMP3_Test_17 | 1
Model | ICFMP3_Test_17 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | [14 empty] | No experimental measurement
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | [14 empty] | No experimental measurement
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | [14 empty] | No experimental measurement
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | [14 empty] | No experimental measurement
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | [14 empty] | No experimental measurement
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | [14 empty] | No experimental measurement
Experiment | ICFMP3_Test_18 | 1
Model | ICFMP3_Test_18 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max | [11 empty] | No experimental measurement
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 121 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 342 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | [14 empty] | No experimental measurement
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 8 | 325 | 363 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 365 | [14 empty] | No experimental measurement
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | [14 empty] | No experimental measurement
Experiment | ICFMP4_Test_1 | 1
Model | ICFMP4_Test_1 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 117 | 136 | 1 | 2 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 117 | 138 | 1 | 3 | 0 | 20 | Min |  |  | 5.7 |  |  | 5.7
Compare | Steel Heat Flux | Surface Temperature | 117 | 186 | 1 | 11 | 0 | 30 | Max
Compare | Concrete Heat Flux | Surface Temperature | 117 | 187 | 1 | 13 | 0 | 30 | Max
Compare | Light Concrete Heat Flux | Surface Temperature | 117 | 188 | 1 | 15 | 0 | 30 | Max
Compare | Steel Heat Temperature | Surface Flux | 117 | 156 | 1 | 10 | 0 | 30 | Max
Compare | Concrete Heat Temperature | Surface Flux | 117 | 155 | 1 | 12 | 0 | 30 | Max
Compare | Light Concrete Heat Temperature | Surface Flux | 117 | 151 | 1 | 14 | 0 | 30 | Max
Compare | M19 Temperature | Surface Temperature | 117 | 139 | 1 | 16 | 0 | 30 | Max
Compare | M20 Temperature | Surface Temperature | 117 | 140 | 1 | 17 | 0 | 30 | Max
Experiment | ICFMP5_Test_4 | 1
Model | ICFMP5_Test_4 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 125 | 168 | 1 | 2 | 0 | 20 | Max
Compare | HGL Height | HGL Height | 125 | 170 | 1 | 3 | 5 | 20 | Min |  |  | 5.6 |  |  | 5.6
Compare | Oxygen | Oxygen | 125 | 293 | 1 | 5 | 0 | 20 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 125 | 295 | 1 | 6 | 0 | 20 | Max
Compare | WS2 Flux | Cable Flux | 125 | 271 | 1 | 11 | 0 | 20 | Max
Compare | WS 3 Flux | Cable Flux | 125 | 172 | 1 | 13 | 0 | 20 | Max |  |  | 0
Compare | WS 4 Flux | Cable Flux | 125 | 273 | 1 | 15 | 0 | 20 | Max
Compare | TCO 1-3 Temperature | Cable Temperature | 125 | 199 | 1 | 18 | 0 | 20 | Max
Compare | TCO 1-5 Temperature | Cable Temperature | 125 | 201 | 1 | 19 | 0 | 20 | Max
Compare | TCO 1-7 Temperature | Cable Temperature | 125 | 203 | 1 | 20 | 0 | 20 | Max
Compare | TCO 3-3 Temperature | Cable Temperature | 125 | 217 | 1 | 21 | 0 | 20 | Max
Compare | TCO 3-5 Temperature | Cable Temperature | 125 | 219 | 1 | 22 | 0 | 20 | Max
Compare | TCO 3-7 Temperature | Cable Temperature | 125 | 221 | 1 | 23 | 0 | 20 | Max |  | -7
Compare | TW 1-1 Temperature | Surface Temperature | 125 | 171 | 1 | 24 | 0 | 20 | Max
Compare | TW 1-4 Temperature | Surface Temperature | 125 | 174 | 1 | 25 | 0 | 20 | Max
Compare | TW 1-7 Temperature | Surface Temperature | 125 | 177 | 1 | 26 | 0 | 20 | Max
Compare | TW 2-1 Temperature | Surface Temperature | 125 | 178 | 1 | 27 | 0 | 20 | Max
Compare | TW 2-4 Temperature | Surface Temperature | 125 | 181 | 1 | 28 | 0 | 20 | Max
Compare | TW 2-7 Temperature | Surface Temperature | 125 | 184 | 1 | 29 | 0 | 20 | Max
Experiment | MV100A | 1
Model | MV100A | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Tree 1 HGL Temperature | HGL Temperature | 271 | 275 | 257 | 258 | 5 | 15 | Max |  |  | 23
Compare | Tree 1 HGL Height | HGL Height | 271 | 273 | 257 | 259 | 5 | 15 | Min |  |  | 2.16 |  |  | 2.16
Compare | Tree 4 HGL Temperature | HGL Temperature | 271 | 279 | 257 | 264 | 5 | 15 | Max |  |  | 23
Compare | Tree 4 HGL Height | HGL Height | 271 | 277 | 257 | 265 | 5 | 15 | Min |  |  | 2.44 |  |  | 2.44
Compare | Tree 5 HGL Temperature | HGL Temperature | 271 | 283 | 257 | 266 | 5 | 15 | Max |  |  | 23
Compare | Tree 5 HGL Height | HGL Height | 271 | 281 | 257 | 267 | 5 | 15 | Min |  |  | 2.44 |  |  | 2.44
Compare | Tree 6 HGL Temperature | HGL Temperature | 271 | 287 | 257 | 268 | 5 | 15 | Max |  |  | 23
Compare | Tree 6 HGL Height | HGL Height | 271 | 285 | 257 | 269 | 5 | 15 | Min |  |  | 2.44 |  |  | 2.44
Experiment | MV100O | 1
Model | MV100O | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Tree 1 HGL Temperature | HGL Temperature | 280 | 284 | 266 | 267 | 5 | 15 | Max |  |  | 21
Compare | Tree 1 HGL Height | HGL Height | 280 | 282 | 266 | 268 | 5 | 15 | Min | Closed |  | 2.16 |  |  | 2.16
Compare | Tree 4 HGL Temperature | HGL Temperature | 280 | 288 | 266 | 273 | 5 | 15 | Max |  |  | 21
Compare | Tree 4 HGL Height | HGL Height | 280 | 286 | 266 | 274 | 5 | 15 | Min | Closed |  | 2.44 |  |  | 2.44
Compare | Tree 5 HGL Temperature | HGL Temperature | 280 | 292 | 266 | 275 | 5 | 15 | Max |  |  | 21
Compare | Tree 5 HGL Height | HGL Height | 280 | 290 | 266 | 276 | 5 | 15 | Min | Closed |  | 2.44 |  |  | 2.44
Compare | Tree 6 HGL Temperature | HGL Temperature | 280 | 296 | 266 | 277 | [5 empty] | 21 | [8 empty] | No experimental measurement
Compare | Tree 6 HGL Height | HGL Height | 280 | 294 | 266 | 278 | 5 | 15 | Min | Closed
Experiment | MV100Z | 1
Model | MV100Z | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Tree 1 HGL Temperature | HGL Temperature | 331 | 335 | 313 | 314 | 5 | 15 | Max |  |  | 22 | [8 empty] | Experimental Peak = 282
Compare | Tree 1 HGL Height | HGL Height | 331 | 333 | 313 | 315 | 5 | 15 | Min |  |  | 2.16 |  |  | 2.16 | [5 empty] | Experimental Peak = 1.0
Compare | Tree 4 HGL Temperature | HGL Temperature | 331 | 339 | 313 | 320 | 5 | 15 | Max |  |  | 22
Compare | Tree 4 HGL Height | HGL Height | 331 | 337 | 313 | 321 | 5 | 15 | Min |  |  | 2.44 |  |  | 2.44
Compare | Tree 5 HGL Temperature | HGL Temperature | 331 | 343 | 313 | 322 | 5 | 15 | Max |  |  | 22
Compare | Tree 5 HGL Height | HGL Height | 331 | 341 | 313 | 323 | 5 | 15 | Min |  |  | 2.44 |  |  | 2.44
Compare | Tree 7 HGL Temperature | HGL Temperature | 331 | 347 | 313 | 328 | 5 | 15 | Max |  |  | 22
Compare | Tree 7 HGL Height | HGL Height | 331 | 345 | 313 | 329 | 5 | 15 | Min |  |  | 2.43 |  |  | 2.43
Experiment | NIST_Plaza | 3
Model | NIST_Plaza | 3
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Burn Room HGL Temperature | HGL Temperature | 1 | 2 | 10 | 11 | 0 | 30 | Max
Compare | Burn Room HGL Height | HGL Height | 1 | [17 empty] | No experimental measurement
Compare | Corridor HGL Temperature | HGL Temperature | 1 | 3 | 10 | 12 | 0 | 30 | Max
Compare | Corridor HGL Height | HGL Height | 1 | [17 empty] | No experimental measurement
Compare | Floor 7 HGL Temperature | HGL Temperature | 1 | 7 | 10 | 16 | 0 | 30 | Max
Compare | Floor 7 HGL Height | HGL Height | 1 | [17 empty] | No experimental measurement
Compare | Corridor Oxygen | Oxygen | 1 | 4 | 10 | 13 | 0 | 30 | Min
Compare | Corridor Carbon Dioxide | Carbon Dioxide | 1 | 6 | 10 | 15 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Corridor 7 Pressure | Pressure | 1 | 8 | 10 | 17 | 0 | 30 | Max
Experiment | fm19 | 5
Model | fm19 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 123 | 114 | 126 | 127 | 0 | 8 | Max
Compare | Room 1 HGL Height | HGL Height | 123 | 14 | 126 | 128 | 0 | 8 | Min |  |  | 2.45
Compare | Room 1 Oxygen | Oxygen | 123 | 20 | 126 | 130 | 0 | 8 | Min
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 123 | 2 | 126 | 131 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 123 |  | 126 | 129 | [14 empty] | No experimental measurement
Compare | Room 2 HGL Temperature | HGL Temperature | 123 | 115 | 126 | 132 | 0 | 8 | Max
Compare | Room 2 HGL Height | HGL Height | 123 | 11 | 126 | 133 | 0 | 8 | Min |  |  | 2.43
Compare | Room 2 HGL Temperature | HGL Temperature | 123 | 116 | 126 | 132 | 0 | 8 | Max
Compare | Room 2 HGL Height | HGL Height | 123 | 12 | 126 | 133 | 0 | 8 | Min |  |  | 2.43
Compare | Room 2 HGL Temperature | HGL Temperature | 123 | 117 | 126 | 132 | 0 | 8 | Max
Compare | Room 2 HGL Height | HGL Height | 123 | 13 | 126 | 133 | 0 | 8 | Min |  |  | 2.43
Compare | Room 2 Oxygen | Oxygen | 123 | 19 | 126 | 135 | 0 | 8 | Min
Compare | Room 2 Carbon Dioxide | Carbon Dioxide | 123 | 1 | 126 | 136 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 2 Pressure | Pressure | 123 |  | 126 | 134 | [14 empty] | No experimental measurement
Compare | Room 3 HGL Temperature | HGL Temperature | 123 | 118 | 126 | 137 | 0 | 8 | Max
Compare | Room 3 HGL Height | HGL Height | 123 | 15 | 126 | 138 | 0 | 8 | Min |  |  | 2.45
Compare | Room 3 Carbon Dioxide | Carbon Dioxide | 123 | 3 | 126 | 141 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 3 Pressure | Pressure | 123 |  | 126 | 139 | [14 empty] | No experimental measurement
Compare | Room 4 HGL Temperature | HGL Temperature | 123 | 119 | 126 | 142 | 0 | 8 | Max
Compare | Room 4 HGL Height | HGL Height | 123 | 16 | 126 | 143 | 0 | 8 | Min |  |  | 2.43
Compare | Room 4 Carbon Dioxide | Carbon Dioxide | 123 | 4 | 126 | 146 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 4 Pressure | Pressure | 123 |  | 126 | 144 | [14 empty] | No experimental measurement
Experiment | fm21 | 5
Model | fm21 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 125 | 116 | 128 | 129 | 0 | 8 | Max
Compare | Room 1 HGL Height | HGL Height | 125 | 16 | 128 | 130 | 0 | 8 | Min |  |  | 2.45
Compare | Room 1 Oxygen | Oxygen | 125 | 22 | 128 | 132 | 0 | 8 | Min
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 125 | 4 | 128 | 133 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 125 |  | 128 | 131 | [14 empty] | No experimental measurement
Compare | Room 2 HGL Temperature | HGL Temperature | 125 | 117 | 128 | 134 | 0 | 8 | Max
Compare | Room 2 HGL Height | HGL Height | 125 | 13 | 128 | 135 | 0 | 8 | Min |  |  | 2.43
Compare | Room 2 HGL Temperature | HGL Temperature | 125 | 118 | 128 | 134 | 0 | 8 | Max
Compare | Room 2 HGL Height | HGL Height | 125 | 14 | 128 | 135 | 0 | 8 | Min |  |  | 2.43
Compare | Room 2 HGL Temperature | HGL Temperature | 125 | 119 | 128 | 134 | 0 | 8 | Max
Compare | Room 2 HGL Height | HGL Height | 125 | 15 | 128 | 135 | 0 | 8 | Min |  |  | 2.43
Compare | Room 2 Oxygen | Oxygen | 125 | 21 | 128 | 137 | 0 | 8 | Min
Compare | Room 2 Carbon Dioxide | Carbon Dioxide | 125 | 1 | 128 | 138 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 2 Carbon Dioxide | Carbon Dioxide | 125 | 2 | 128 | 138 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 2 Pressure | Pressure | 125 |  | 128 | 136 | [14 empty] | No experimental measurement
Compare | Room 3 HGL Temperature | HGL Temperature | 125 | 120 | 128 | 139 | 0 | 8 | Max
Compare | Room 3 HGL Height | HGL Height | 125 | 17 | 128 | 140 | 0 | 8 | Min |  |  | 2.45
Compare | Room 3 Carbon Dioxide | Carbon Dioxide | 125 | 5 | 128 | 143 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 3 Pressure | Pressure | 125 |  | 128 | 141 | [14 empty] | No experimental measurement
Compare | Room 4 HGL Temperature | HGL Temperature | 125 | 120 | 128 | 144 | 0 | 8 | Max
Compare | Room 4 HGL Height | HGL Height | 125 | 18 | 128 | 145 | 0 | 8 | Min |  |  | 2.43
Compare | Room 4 Carbon Dioxide | Carbon Dioxide | 125 | 6 | 128 | 148 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 4 Pressure | Pressure | 125 |  | 128 | 146 | [14 empty] | No experimental measurement
Experiment | 1Room1 | 5
Model | 1Room1 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature A | HGL Temperature | 87 | 85 | 109 | 110 | 0 | 30 | Max
Compare | Room 1 HGL Height A | HGL Height | 87 | 11 | 109 | 111 | 0 | 30 | Min |  |  | 2.31
Compare | Room 1 HGL Temperature B | HGL Temperature | 87 | 86 | 109 | 110 | 0 | 30 | Max
Compare | Room 1 HGL Height B | HGL Height | 87 | 12 | 109 | 111 | 0 | 30 | Min |  |  | 2.31
Compare | Room 1 Oxygen A | Oxygen | 87 | 21 | 109 | 113 | 0 | 30 | Min
Compare | Room 1 Carbon Dioxide A | Carbon Dioxide | 87 | 3 | 109 | 114 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Room 1 Oxygen B | Oxygen | 87 | 22 | 109 | 113 | 0 | 30 | Min
Compare | Room 1 Carbon Dioxide B | Carbon Dioxide | 87 | 4 | 109 | 114 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 87 |  | 109 | 112 | [14 empty] | No experimental measurement
Experiment | 1Room6 | 5
Model | 1Room6 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature A | HGL Temperature | 87 | 85 | 113 | 114 | 0 | 30 | Max
Compare | Room 1 HGL Height A | HGL Height | 87 | 11 | 113 | 115 | 0 | 30 | Min |  |  | 2.31
Compare | Room 1 HGL Temperature B | HGL Temperature | 87 | 86 | 113 | 114 | 0 | 30 | Max
Compare | Room 1 HGL Height B | HGL Height | 87 | 12 | 113 | 115 | 0 | 30 | Min |  |  | 2.31
Compare | Room 1 Oxygen A | Oxygen | 87 | 21 | 113 | 117 | 0 | 30 | Min
Compare | Room 1 Carbon Dioxide A | Carbon Dioxide | 87 | 3 | 113 | 118 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Room 1 Oxygen B | Oxygen | 87 | 22 | 113 | 117 | 0 | 30 | Min
Compare | Room 1 Carbon Dioxide B | Carbon Dioxide | 87 | 4 | 113 | 118 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 87 |  | 113 | 116 | [14 empty] | No experimental measurement
Experiment | 1RWall1 | 5
Model | 1RWall1 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 83 | 82 | 110 | 111 | 0 | 30 | Max
Compare | Room 1 HGL Height | HGL Height | 83 | 8 | 110 | 112 | 0 | 30 | Min |  |  | 2.44
Compare | Room 1 Oxygen | Oxygen | 83 |  | 110 | 114
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 83 |  | 110 | 115 | [5 empty] | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 83 | 32 | 110 | 113 | 0 | 30 | Min
Experiment | 1RWall2 | 5
Model | 1RWall2 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 105 | 104 | 133 | 134 | 0 | 10 | Max
Compare | Room 1 HGL Height | HGL Height | 105 | 8 | 133 | 135 | 0 | 10 | Min |  |  | 2.44
Compare | Room 1 Oxygen | Oxygen | 105 |  | 133 | 137
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 105 |  | 133 | 138 | [5 empty] | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 105 | 32 | 133 | 136 | 0 | 10 | Min
End

## Output
NRC Comparisons
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
Experiment | FM_SNL_Test_4_Exp | 2
Model | FM_SNL_Test_4_Mod | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 3 | 1 | 2 | 0 | 15 | Max |  |  | 12.68 | 71.867 | 10 | 15 | 83.938 | 10 | 59.187 | 68.938 | 16.476
Compare | HGL Height | HGL Height | 1 | 2 | 1 | 3 | 0 | 15 | Min | Closed |  | 6.1 | 2.698 | 6.3333 | 6.1 | 0.57267 | 14.833 | -3.402 | -5.5273
Compare | Temperature 1/0.98H | Ceiling Jet Temperature | 5 | 6 | 1 | 9 | 0 | 15 | Max |  |  | 16.4 | 98.58 | 10 | 15 | 148.49 | 10 | 82.18 | 133.49 | 62.434
Compare | Temperature 11/0.98H | Ceiling Jet Temperature | 5 | 16 | 1 | 8 | 0 | 15 | Max |  |  | 15.4 | 81.18 | 10 | 15 | 117.45 | 10 | 65.78 | 102.45 | 55.745
Experiment | FM_SNL_Test_5 | 2
Model | FM_SNL_Test_5 | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 11 | 13 | 1 | 2 | 0 | 15 | Max |  |  | 21 | 65.465 | 10 | 20 | 69.21 | 10 | 44.465 | 49.21 | 10.672
Compare | HGL Height | HGL Height | 11 | 12 | 1 | 3 | 0 | 15 | Min | Closed |  | 6.1 | 3.1845 | 5.5 | 6.1 | 0.49275 | 13.167 | -2.9155 | -5.6073
Compare | Temperature 1/0.98H | Ceiling Jet Temperature | 15 | 16 | 1 | 9 | 0 | 15 | Max |  |  | 21.1 | 91.519 | 10 | 20 | 121.07 | 10 | 70.419 | 101.07 | 43.523
Compare | Temperature 11/0.98H | Ceiling Jet Temperature | 15 | 26 | 1 | 8 | 0 | 15 | Max |  |  | 20.6 | 73.16 | 10.167 | 20 | 94.983 | 10 | 52.56 | 74.983 | 42.662
Experiment | FM_SNL_Test_21 | 2
Model | FM_SNL_Test_21 | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 11 | 13 | 1 | 2 | 0 | 30 | Max |  |  | 17.7 | 83.66 | 19 | 15 | 102.97 | 19 | 65.96 | 87.966 | 33.363
Compare | HGL Height | HGL Height | 11 | 12 | 1 | 3 | 0 | 30 | Min | Closed |  | 6.1 | 2.6701 | 7.1667 | 6.1 | 0.013373 | 28.833 | -3.4299 | -6.0866
Compare | Temperature 1/0.98H | Ceiling Jet Temperature | 15 | 16 | 1 | 9 | 0 | 30 | Max |  |  | 18.2 | 92.704 | 19.167 | 15 | 174 | 19 | 74.504 | 159 | 113.41
Compare | Temperature 11/0.98H | Ceiling Jet Temperature | 15 | 26 | 1 | 8 | 0 | 30 | Max |  |  | 17.2 | 94.396 | 19.167 | 15 | 139.3 | 19 | 77.196 | 124.3 | 61.021
Experiment | ICFMP2_Case_1 | 1
Model | ICFMP2_Case_1 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 83 | 34 | 35 | 0 | 8 | Max |  |  | 20.9 | 75.66 | 7 | 20 | 82.337 | 7 | 54.76 | 62.337 | 13.836
Compare | HGL Height | HGL Height | 1 | 81 | 34 | 36 | 0 | 8 | Min | Closed |  | 19 | 4.4483 | 7.8333 | 19 | 1.7116 | 6.8333 | -14.552 | -17.288
Experiment | ICFMP2_Case_2 | 1
Model | ICFMP2_Case_2 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 4 | 6 | 7 | 0 | 8 | Max |  |  | 23.04 | 109.35 | 6 | 20 | 119.28 | 6.3333 | 86.31 | 99.282 | 15.03
Compare | HGL Height | HGL Height | 1 | 2 | 6 | 8 | 0 | 8 | Min | Closed |  | 19 | 4.2333 | 6.8333 | 19 | 1.0192 | 6 | -14.767 | -17.981
Experiment | ICFMP2_Case_3 | 1
Model | ICFMP2_Case_3 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 46 | 35 | 36 | 0 | 8 | Max |  |  | 22.47 | 105.03 | 5 | 20 | 110.99 | 5.5 | 82.56 | 90.994 | 10.216
Compare | HGL Height | HGL Height | 1 | 44 | 35 | 37 | 0 | 8 | Min |  |  | 19 | 5.14 | 5 | 19 | 4.0554 | 4.8333 | -13.86 | -14.945 | 7.8253
Experiment | ICFMP3_Test_1 | 1
Model | ICFMP3_Test_1 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 20.89 | 143.78 | 22.667 | 22 | 157.48 | 22.667 | 122.89 | 135.48 | 10.246
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.78 | 26.667 | 3.82 | 0.007133 | 22.5 | -3.04 | -3.8129
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 20.1 | 175 | 22.667 | 22 | 157.48 | 22.667 | 154.9 | 135.48 | -12.536
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.144 | 23.833 | 0.20535 | 0.12924 | 24.667 | -0.065 | -0.076107 | 17.088
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.0384 | 24.5 | 0 | 0.044425 | 24.667 | 0.0384 | 0.044425 | 15.691
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 41.5 | 26.833 | 0 | 319.84 | 29.833 | 41.5 | 319.84 | 670.69
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 57.6 | 3.1667 | 0 | 42.398 | 2.5 | 57.6 | 42.398 | -26.392
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 23.6 | 130 | 23.833 | 22 | 124.77 | 23.833 | 106.4 | 102.77 | -3.4098
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | [14 empty] | No experimental measureme
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 23.4 | 106 | 23.667 | 22 | 89.864 | 23.333 | 82.6 | 67.864 | -17.84
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 23.5 | 87.9 | 24.333 | 22 | 117.96 | 23.833 | 64.4 | 95.956 | 49
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 18.1 | 72.3 | 24.167 | 22 | 110.94 | 23.333 | 54.2 | 88.945 | 64.105
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 339 | 0 | 30 | Max |  |  | 19.9 | 87.9 | 23.167 | 22 | 110.99 | 23.167 | 68 | 88.994 | 30.874
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 17 | 72.4 | 24.333 | 22 | 110.51 | 23.333 | 55.4 | 88.51 | 59.765
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 17.3 | 88.3 | 23.167 | 22 | 111.12 | 23.333 | 71 | 89.118 | 25.518
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 17.2 | 55.4 | 24.5 | 22 | 92.94 | 23.167 | 38.2 | 70.94 | 85.706
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max |  |  | 18.2 | 95.6 | 22.833 | 22 | 91.214 | 23.167 | 77.4 | 69.214 | -10.576
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 21.3 | 102 | 22.5 | 22 | 113.93 | 23.333 | 80.7 | 91.93 | 13.916
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 22.7 | 199 | 22.333 | 22 | 112.61 | 23.167 | 176.3 | 90.61 | -48.605
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.00297 | 1.85 | 21.667 | 0 | 1.6738 | 22.5 | 1.853 | 1.6738 | -9.6679
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | [14 empty] | No experimental measureme
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.0157 | 1.62 | 19.667 | 0 | 1.7999 | 22.5 | 1.6043 | 1.7999 | 12.194
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | [14 empty] | No experimental measureme
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.00149 | 1.12 | 22.667 | 0 | 1.5319 | 22.5 | 1.1215 | 1.5319 | 36.594
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | -0.00936 | 1.43 | 22.5 | 0 | 1.5832 | 22.5 | 1.4394 | 1.5832 | 9.9949
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | 0.00108 | 0.868 | 22.667 | 0 | 1.4342 | 22.5 | 0.86692 | 1.4342 | 65.435
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.00106 | 1.51 | 21.667 | 0 | 1.5881 | 22.5 | 1.5111 | 1.5881 | 5.0973
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | -0.014363 | 1.3705 | 23.167 | 0 | 1.6716 | 22.5 | 1.3849 | 1.6716 | 20.708
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 362 | 0 | 30 | Max |  |  | -0.0056417 | 1.7601 | 22.5 | 0 | 1.6525 | 22.5 | 1.7657 | 1.6525 | -6.4115
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max |  |  | -0.0050462 | 1.2532 | 23.333 | 0 | 1.6706 | 22.5 | 1.2583 | 1.6706 | 32.767
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | -0.017821 | 1.7044 | 23 | 0 | 1.6669 | 22.5 | 1.7222 | 1.6669 | -3.2117
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | -0.026425 | 0.89798 | 23.5 | 0 | 1.3695 | 22.5 | 0.92441 | 1.3695 | 48.145
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | -0.0077126 | 2.3751 | 11.5 | 0 | 1.3363 | 22.5 | 2.3828 | 1.3363 | -43.92
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | -0.014351 | 1.9142 | 22.167 | 0 | 1.7032 | 22.5 | 1.9286 | 1.7032 | -11.684
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max |  |  | 0.03481 | 3.7889 | 22.667 | 0 | 1.6687 | 22.5 | 3.7541 | 1.6687 | -55.55
Experiment | ICFMP3_Test_2 | 1
Model | ICFMP3_Test_2 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 24.03 | 253.24 | 10.167 | 26 | 260.57 | 10.333 | 229.21 | 234.57 | 2.3367
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.82 | 11.667 | 3.82 | 0.011216 | 10.333 | -3 | -3.8088
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 23.4 | 294 | 9.8333 | 26 | 260.57 | 10.333 | 270.6 | 234.57 | -13.316
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.117 | 10.333 | 0.20471 | 0.10423 | 10.333 | -0.092 | -0.10048 | 9.2196
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.0543 | 10.333 | 0 | 0.058653 | 10.333 | 0.0543 | 0.058653 | 8.0162
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 128 | 8 | 0 | 418.82 | 20 | 128 | 418.82 | 227.2
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 290 | 2 | 0 | 266.01 | 3 | 290 | 266.01 | -8.2721
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 26.3 | 202 | 10.167 | 26 | 169.98 | 10.333 | 175.7 | 143.98 | -18.056
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 26.7 | 153 | 10.167 | 26 | 171.47 | 10.333 | 126.3 | 145.47 | 15.177
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 26.1 | 155 | 10.333 | 26 | 138.25 | 10.333 | 128.9 | 112.25 | -12.92
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 26.4 | 133 | 10.5 | 26 | 164.22 | 10.333 | 106.6 | 138.22 | 29.662
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 21.4 | 117 | 10.667 | 26 | 176.35 | 10.5 | 95.6 | 150.35 | 57.266
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 342 | 0 | 30 | Max |  |  | 22.9 | 143 | 10.333 | 26 | 177.34 | 10.333 | 120.1 | 151.34 | 26.014
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 20.4 | 130 | 10.667 | 26 | 175.77 | 10.5 | 109.6 | 149.77 | 36.651
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 20.6 | 146 | 10.333 | 26 | 176.61 | 10.5 | 125.4 | 150.61 | 20.102
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 20.7 | 94.9 | 10.833 | 26 | 153.01 | 10.333 | 74.2 | 127.01 | 71.166
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max |  |  | 21.8 | 178 | 7.5 | 26 | 149.53 | 10.333 | 156.2 | 123.53 | -20.915
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 24.2 | 172 | 10.333 | 26 | 180.15 | 10.5 | 147.8 | 154.15 | 4.293
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 25.8 | 334 | 9.8333 | 26 | 178.01 | 10.333 | 308.2 | 152.01 | -50.678
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.000495 | 5.26 | 9.8333 | 0 | 4.6139 | 10.333 | 5.2605 | 4.6139 | -12.291
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.0373 | 9.79 | 10.167 | 0 | 4.7519 | 10.333 | 9.8273 | 4.7519 | -51.646
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.00705 | 4.78 | 10.167 | 0 | 4.5654 | 10.333 | 4.773 | 4.5654 | -4.348
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | [14 empty] | No experimental measureme
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.00241 | 2.88 | 7.1667 | 0 | 4.1845 | 10.333 | 2.8824 | 4.1845 | 45.174
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.00379 | 4.16 | 10.167 | 0 | 4.3326 | 10.333 | 4.1562 | 4.3326 | 4.2434
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -4.71e-05 | 1.99 | 10.167 | 0 | 3.903 | 10.333 | 1.99 | 3.903 | 96.126
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | 0.00213 | 5.97 | 4.6667 | 0 | 4.3407 | 10.333 | 5.9679 | 4.3407 | -27.265
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.020916 | 3.7959 | 10.5 | 0 | 4.4026 | 10.333 | 3.775 | 4.4026 | 16.627
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 365 | 0 | 30 | Max |  |  | 0.028684 | 4.5411 | 10.167 | 0 | 4.3435 | 10.333 | 4.5124 | 4.3435 | -3.7422
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max |  |  | 0.03132 | 3.652 | 10.167 | 0 | 4.397 | 10.333 | 3.6207 | 4.397 | 21.44
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.019552 | 4.6396 | 10.167 | 0 | 4.3911 | 10.333 | 4.62 | 4.3911 | -4.9545
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.011088 | 2.603 | 10.333 | 0 | 3.6517 | 10.333 | 2.5919 | 3.6517 | 40.892
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | 0.029536 | 8.9321 | 6.6667 | 0 | 3.5445 | 10.333 | 8.9025 | 3.5445 | -60.186
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.022079 | 5.6693 | 10 | 0 | 4.4656 | 10.333 | 5.6472 | 4.4656 | -20.923
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max |  |  | 0.0626 | 14.57 | 9.8333 | 0 | 4.3415 | 10.333 | 14.507 | 4.3415 | -70.073
Experiment | ICFMP3_Test_3 | 1
Model | ICFMP3_Test_3 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 27.84 | 235.09 | 23.5 | 30 | 273.33 | 23 | 207.25 | 243.33 | 17.409
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 | 0.91 | 21.333 | 3.82 | 1.0068 | 3.6667 | -2.91 | -2.8132 | -3.3265
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 27.135 | 267.8 | 22.833 | 30 | 273.33 | 23 | 240.67 | 243.33 | 1.1062
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.20944 | 0.15732 | 23.167 | 0.20423 | 0.16018 | 12.667 | -0.052125 | -0.044054 | -15.484
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.031099 | 23.167 | 0 | 0.027337 | 13.667 | 0.031099 | 0.027337 | -12.098
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 118.03 | 21.667 | 0 | 139.61 | 10.667 | 118.03 | 139.61 | 18.28
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 | -1.907 | 26 | 0 | -2.1026 | 23.667 | -1.907 | -2.1026 | 10.259
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 29.977 | 255.91 | 23.5 | 30 | 251.37 | 23.5 | 225.93 | 221.37 | -2.0181
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 30.854 | 240.54 | 24.333 | 30 | 252.55 | 23.5 | 209.68 | 222.55 | 6.1348
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 30.122 | 225.48 | 24.167 | 30 | 189.54 | 23.333 | 195.36 | 159.54 | -18.336
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 29.997 | 198.71 | 24 | 30 | 254.18 | 23.333 | 168.72 | 224.18 | 32.874
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 26.441 | 140.77 | 24.333 | 30 | 217.23 | 23.333 | 114.33 | 187.23 | 63.767
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 26.036 | 198.42 | 23.667 | 30 | 232.94 | 23.167 | 172.39 | 202.94 | 17.726
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 24.104 | 111.39 | 23.667 | 30 | 182.2 | 23.333 | 87.285 | 152.2 | 74.374
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 24.414 | 170.2 | 23.833 | 30 | 220.95 | 23.333 | 145.78 | 190.95 | 30.986
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 25.121 | 78.72 | 24.5 | 30 | 172.73 | 23.5 | 53.598 | 142.73 | 166.29
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 24.727 | 143.41 | 23.333 | 30 | 168.6 | 23.5 | 118.69 | 138.6 | 16.78
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 29.472 | 184.68 | 24.167 | 30 | 224.16 | 23.333 | 155.21 | 194.16 | 25.097
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 28.933 | 316.31 | 23.5 | 30 | 227.41 | 23.167 | 287.38 | 197.41 | -31.306
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.012377 | 7.0906 | 20.833 | 0 | 4.9384 | 23 | 7.103 | 4.9384 | -30.475
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.013617 | 9.4402 | 22 | 0 | 5.1082 | 23 | 9.4539 | 5.1082 | -45.967
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.015241 | 5.5332 | 20.833 | 0 | 4.9039 | 23 | 5.5485 | 4.9039 | -11.617
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.023208 | 6.4269 | 22.333 | 0 | 5.5111 | 23 | 6.4501 | 5.5111 | -14.559
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.0010343 | 4.4462 | 23.167 | 0 | 4.8761 | 23 | 4.4473 | 4.8761 | 9.6435
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | [14 empty] | No experimental measureme
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.00033982 | 2.9525 | 23.167 | 0 | 4.5264 | 23 | 2.9529 | 4.5264 | 53.289
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | 0.0011116 | 5.364 | 3.6667 | 0 | 5.4724 | 23 | 5.3629 | 5.4724 | 2.0413
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.073065 | 3.5717 | 21.833 | 0 | 4.4532 | 23 | 3.4986 | 4.4532 | 27.284
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.067871 | 4.3884 | 23.667 | 0 | 5.0084 | 23 | 4.3205 | 5.0084 | 15.92
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max |  |  | 0.072635 | 2.6014 | 23.5 | 0 | 3.5956 | 23 | 2.5288 | 3.5956 | 42.185
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.057654 | 4.5037 | 23 | 0 | 4.5805 | 23 | 4.446 | 4.5805 | 3.0235
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.060932 | 2.0321 | 23.167 | 0 | 3.1937 | 23 | 1.9712 | 3.1937 | 62.018
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max |  |  | 0.061399 | 4.133 | 20.833 | 0 | 3.0854 | 23 | 4.0716 | 3.0854 | -24.222
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.07498 | 4.6919 | 22.167 | 0 | 4.6603 | 23 | 4.6169 | 4.6603 | 0.93814
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max |  |  | 0.1012 | 9.9776 | 22.333 | 0 | 4.7752 | 23 | 9.8764 | 4.7752 | -51.651
Experiment | ICFMP3_Test_4 | 1
Model | ICFMP3_Test_4 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 24.83 | 229.11 | 13.333 | 27 | 248.66 | 13.5 | 204.28 | 221.66 | 8.5104
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.56 | 19.833 | 3.82 | 0.017876 | 13.5 | -3.26 | -3.8021
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 23.776 | 252.46 | 12.833 | 27 | 248.66 | 13.5 | 228.69 | 221.66 | -3.0705
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.20936 | 0.13075 | 13.833 | 0.20398 | 0.14412 | 13.5 | -0.078605 | -0.059864 | -23.842
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.04737 | 13.833 | 0 | 0.034985 | 13.5 | 0.04737 | 0.034985 | -26.146
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 79.898 | 8.3333 | 0 | 177.26 | 13.5 | 79.898 | 177.26 | 121.86
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 56.605 | 1.5 | 0 | 76.776 | 3 | 56.605 | 76.776 | 35.636
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 26.245 | 175 | 13.667 | 27 | 182.53 | 13.5 | 148.76 | 155.53 | 4.548
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 26.249 | 139.38 | 13.667 | 27 | 183.78 | 13.5 | 113.13 | 156.78 | 38.582
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 25.917 | 174.46 | 13.667 | 27 | 142.26 | 13.5 | 148.55 | 115.26 | -22.411
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 26.298 | 151.23 | 13.333 | 27 | 175.54 | 13.5 | 124.93 | 148.54 | 18.897
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 21.658 | 118.59 | 13.667 | 27 | 176.61 | 13.5 | 96.934 | 149.61 | 54.344
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 342 | 0 | 30 | Max |  |  | 22.687 | 168.19 | 13.5 | 27 | 178.51 | 13.5 | 145.5 | 151.51 | 4.1264
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 20.175 | 125.98 | 13.667 | 27 | 176.18 | 13.5 | 105.81 | 149.18 | 40.989
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 20.434 | 141.29 | 13.667 | 27 | 176.69 | 13.5 | 120.85 | 149.69 | 23.86
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 20.421 | 96.782 | 13.667 | 27 | 156.75 | 13.5 | 76.361 | 129.75 | 69.919
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 354 | 0 | 30 | Max |  |  | 21.444 | 173.14 | 13.167 | 27 | 153.84 | 13.5 | 151.7 | 126.84 | -16.384
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 24.529 | 171.78 | 13.667 | 27 | 179.89 | 13.5 | 147.25 | 152.89 | 3.8265
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 24.89 | 204.92 | 12.5 | 27 | 179.67 | 13.5 | 180.03 | 152.67 | -15.2
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.032836 | 5.4899 | 13 | 0 | 4.1411 | 13.5 | 5.5227 | 4.1411 | -25.017
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.10225 | 7.1274 | 12.5 | 0 | 4.2705 | 13.5 | 7.2296 | 4.2705 | -40.931
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.059657 | 5.0832 | 12.5 | 0 | 4.1579 | 13.5 | 5.0236 | 4.1579 | -17.233
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.19744 | 6.2271 | 13.167 | 0 | 4.2281 | 13.5 | 6.4245 | 4.2281 | -34.189
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | 0.0026421 | 2.9189 | 12.333 | 0 | 3.859 | 13.5 | 2.9162 | 3.859 | 32.328
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.0026776 | 3.2577 | 12.333 | 0 | 3.9958 | 13.5 | 3.255 | 3.9958 | 22.759
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.00093734 | 2.0218 | 13.5 | 0 | 3.6031 | 13.5 | 2.0227 | 3.6031 | 78.13
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | 0.00033777 | 5.9965 | 7.1667 | 0 | 3.9824 | 13.5 | 5.9962 | 3.9824 | -33.584
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.026416 | 3.4366 | 13.167 | 0 | 3.9546 | 13.5 | 3.4102 | 3.9546 | 15.965
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.033877 | 3.5407 | 13.5 | 0 | 3.9523 | 13.5 | 3.5068 | 3.9523 | 12.701
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max |  |  | 0.033957 | 3.2944 | 13.5 | 0 | 3.9493 | 13.5 | 3.2605 | 3.9493 | 21.127
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.020909 | 3.995 | 13.5 | 0 | 3.9457 | 13.5 | 3.9741 | 3.9457 | -0.71463
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.010446 | 2.4762 | 13.333 | 0 | 3.3261 | 13.5 | 2.4658 | 3.3261 | 34.891
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | 0.033587 | 8.5444 | 7 | 0 | 3.2435 | 13.5 | 8.5108 | 3.2435 | -61.89
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.027313 | 5.1111 | 12.667 | 0 | 4.0064 | 13.5 | 5.0838 | 4.0064 | -21.191
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max |  |  | 0.060767 | 6.0799 | 3.1667 | 0 | 3.9623 | 13.5 | 6.0192 | 3.9623 | -34.172
Experiment | ICFMP3_Test_5 | 1
Model | ICFMP3_Test_5 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 25.02 | 200.51 | 23.167 | 28 | 226.17 | 23 | 175.49 | 198.17 | 12.922
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 | 0.87 | 28.833 | 3.82 | 1.1571 | 4 | -2.95 | -2.663 | -9.7305
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 23.554 | 231.29 | 21.333 | 28 | 226.17 | 23 | 207.74 | 198.17 | -4.6082
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.20942 | 0.17906 | 17 | 0.20433 | 0.1783 | 8.8333 | -0.030366 | -0.02603 | -14.28
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.017468 | 6.5 | 0 | 0.016122 | 10.167 | 0.017468 | 0.016122 | -7.7014
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 87.335 | 22.167 | 0 | 90.568 | 8 | 87.335 | 90.568 | 3.7023
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 | -1.8097 | 25.5 | 0 | -1.9599 | 23.667 | -1.8097 | -1.9599 | 8.2963
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 26.655 | 177 | 23.667 | 28 | 210.79 | 23.333 | 150.34 | 182.79 | 21.58
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 26.538 | 158.93 | 23.833 | 28 | 212.24 | 23.333 | 132.39 | 184.24 | 39.164
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 26.282 | 201.16 | 23.5 | 28 | 155.91 | 23.167 | 174.88 | 127.91 | -26.858
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 26.875 | 187.88 | 23.833 | 28 | 218.26 | 23.333 | 161 | 190.26 | 18.175
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 23.332 | 117.05 | 23.833 | 28 | 173.67 | 23.333 | 93.718 | 145.67 | 55.435
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 23.59 | 178.15 | 23.667 | 28 | 196.06 | 23.167 | 154.56 | 168.06 | 8.7326
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 21.571 | 92.965 | 21.333 | 28 | 143.78 | 23.333 | 71.394 | 115.78 | 62.172
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 21.547 | 139.14 | 23.5 | 28 | 175.88 | 23.333 | 117.59 | 147.88 | 25.756
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 22.272 | 63.926 | 24 | 28 | 134.86 | 23.333 | 41.655 | 106.86 | 156.53
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 354 | 0 | 30 | Max |  |  | 22.033 | 192.8 | 23.333 | 28 | 132.33 | 23.333 | 170.76 | 104.33 | -38.905
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 26.149 | 151.42 | 23 | 28 | 179.15 | 23.333 | 125.27 | 151.15 | 20.663
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max |  |  | 25.783 | 289.19 | 23.167 | 28 | 186.77 | 23.167 | 263.41 | 158.77 | -39.726
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.062047 | 6.7977 | 20.167 | 0 | 3.647 | 23 | 6.8597 | 3.647 | -46.835
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.1527 | 8.3624 | 20.833 | 0 | 3.7799 | 23 | 8.5151 | 3.7799 | -55.609
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.076532 | 6.5252 | 21 | 0 | 3.6386 | 23 | 6.4487 | 3.6386 | -43.575
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.10863 | 6.5766 | 22 | 0 | 4.2338 | 22.833 | 6.6852 | 4.2338 | -36.669
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.0014911 | 3.8828 | 21 | 0 | 3.605 | 23 | 3.8843 | 3.605 | -7.1896
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | -0.00557 | 4.7761 | 19.833 | 0 | 3.7432 | 23 | 4.7816 | 3.7432 | -21.716
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | 0.0015763 | 2.6478 | 23.167 | 0 | 3.3154 | 23 | 2.6462 | 3.3154 | 25.289
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | 0.00038648 | 5.4468 | 23 | 0 | 4.22 | 22.833 | 5.4464 | 4.22 | -22.518
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.044626 | 2.7293 | 23.333 | 0 | 3.0679 | 23 | 2.6847 | 3.0679 | 14.273
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.043562 | 3.8565 | 23 | 0 | 3.7265 | 23 | 3.8129 | 3.7265 | -2.2663
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max |  |  | 0.045851 | 2.0441 | 21.167 | 0 | 2.5357 | 23 | 1.9983 | 2.5357 | 26.895
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.028351 | 3.3201 | 23.5 | 0 | 3.1221 | 23 | 3.2917 | 3.1221 | -5.1516
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.033025 | 1.4328 | 23.333 | 0 | 2.1874 | 23 | 1.3997 | 2.1874 | 56.274
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | 0.049203 | 10.104 | 7.1667 | 0 | 2.1351 | 23 | 10.055 | 2.1351 | -78.766
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.044614 | 3.4162 | 22.667 | 0 | 3.1846 | 23 | 3.3715 | 3.1846 | -5.5434
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | 0 | 30 | Max |  |  | 0.069552 | 6.8097 | 23 | 0 | 3.414 | 23 | 6.7402 | 3.414 | -49.349
Experiment | ICFMP3_Test_7 | 1
Model | ICFMP3_Test_7 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 22.17 | 138.98 | 22.333 | 24 | 156.52 | 22.333 | 116.81 | 132.52 | 13.452
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.77 | 25.5 | 3.82 | 0.0071967 | 22.167 | -3.05 | -3.8128
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 21.583 | 160.89 | 22.333 | 24 | 156.52 | 22.333 | 139.31 | 132.52 | -4.8704
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.20921 | 0.14529 | 23.333 | 0.20366 | 0.13066 | 24.167 | -0.063915 | -0.072999 | 14.213
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.037978 | 23.333 | 0 | 0.042644 | 24.167 | 0.037978 | 0.042644 | 12.287
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 55.051 | 27.833 | 0 | 306.14 | 28.833 | 55.051 | 306.14 | 456.09
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 45.871 | 2.8333 | 0 | 28.842 | 2.1667 | 45.871 | 28.842 | -37.123
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 24.526 | 133.75 | 23 | 24 | 125.95 | 23.167 | 109.22 | 101.95 | -6.6576
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 25.27 | 112.53 | 23 | 24 | 126.25 | 23 | 87.264 | 102.25 | 17.17
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 23.92 | 114.03 | 23.333 | 24 | 97.313 | 22.833 | 90.107 | 73.313 | -18.638
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 24.074 | 102.13 | 23 | 24 | 117.24 | 23.333 | 78.053 | 93.242 | 19.46
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 19.094 | 72.229 | 23.5 | 24 | 110.5 | 22.833 | 53.134 | 86.5 | 62.795
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 342 | 0 | 30 | Max |  |  | 20.99 | 91.28 | 22.833 | 24 | 110.57 | 22.833 | 70.29 | 86.57 | 23.162
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max |  |  | 18.209 | 72.832 | 23.833 | 24 | 110.12 | 22.833 | 54.624 | 86.122 | 57.664
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 18.519 | 88.673 | 22.833 | 24 | 110.7 | 22.833 | 70.155 | 86.704 | 23.59
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 18.277 | 54.634 | 22.833 | 24 | 92.635 | 22.667 | 36.357 | 68.635 | 88.782
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max |  |  | 19.429 | 97.636 | 22.667 | 24 | 90.936 | 22.667 | 78.206 | 66.936 | -14.412
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 22.618 | 102.51 | 22.5 | 24 | 113.49 | 22.833 | 79.891 | 89.487 | 12.011
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 23.684 | 215.09 | 21 | 24 | 112.15 | 22.667 | 191.41 | 88.149 | -53.946
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.0037954 | 1.8362 | 22.833 | 0 | 1.6273 | 22.167 | 1.84 | 1.6273 | -11.558
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.048797 | 2.4691 | 22.5 | 0 | 1.6752 | 22.167 | 2.5179 | 1.6752 | -33.468
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.0070468 | 1.5018 | 20.833 | 0 | 1.7076 | 22.167 | 1.5088 | 1.7076 | 13.176
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.021325 | 1.8703 | 22.5 | 0 | 1.6908 | 22.167 | 1.8916 | 1.6908 | -10.617
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | 0.0027528 | 1.2069 | 22 | 0 | 1.5004 | 22.167 | 1.2041 | 1.5004 | 24.605
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.0008912 | 1.3498 | 22 | 0 | 1.5507 | 22.167 | 1.3489 | 1.5507 | 14.955
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.0020197 | 0.81845 | 22.333 | 0 | 1.4046 | 22.167 | 0.82047 | 1.4046 | 71.195
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | 0.00028986 | 1.4707 | 19.833 | 0 | 1.5558 | 22.167 | 1.4704 | 1.5558 | 5.8111
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | -0.0080703 | 1.3709 | 22.333 | 0 | 1.6397 | 22.333 | 1.379 | 1.6397 | 18.902
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 365 | 0 | 30 | Max |  |  | 0.00046138 | 1.8773 | 21.833 | 0 | 1.6196 | 22.167 | 1.8768 | 1.6196 | -13.704
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | -0.015223 | 1.2064 | 22.167 | 0 | 1.6403 | 22.333 | 1.2216 | 1.6403 | 34.277
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | -0.005005 | 1.7821 | 22.833 | 0 | 1.6349 | 22.333 | 1.7871 | 1.6349 | -8.5166
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | -0.018805 | 0.88373 | 22.667 | 0 | 1.3406 | 22.167 | 0.90253 | 1.3406 | 48.542
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | 0.0025534 | 2.322 | 10.5 | 0 | 1.3078 | 22.167 | 2.3194 | 1.3078 | -43.614
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | -0.0051942 | 1.9366 | 22.333 | 0 | 1.6704 | 22.333 | 1.9418 | 1.6704 | -13.977
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372
Experiment | ICFMP3_Test_8 | 1
Model | ICFMP3_Test_8 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 28.84 | 246.52 | 10 | 25 | 259.06 | 10.167 | 217.68 | 234.06 | 7.5234
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.81 | 11.833 | 3.82 | 0.011432 | 10.167 | -3.01 | -3.8086
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 30.708 | 277.64 | 9.6667 | 25 | 259.06 | 10.167 | 246.93 | 234.06 | -5.2135
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.20913 | 0.11307 | 10.667 | 0.20312 | 0.10488 | 10.333 | -0.096062 | -0.09824 | 2.2675
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.057883 | 10.667 | 0 | 0.057377 | 10.333 | 0.057883 | 0.057377 | -0.87288
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 99.528 | 8 | 0 | 410.64 | 20.333 | 99.528 | 410.64 | 312.58
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 189.34 | 2 | 0 | 213.95 | 3 | 189.34 | 213.95 | 13
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 28.854 | 212.16 | 10 | 25 | 167 | 10.167 | 183.31 | 142 | -22.535
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 29.447 | 179.08 | 10 | 25 | 168.53 | 10.167 | 149.63 | 143.53 | -4.0769
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 28.743 | 160.14 | 10 | 25 | 135.95 | 10.167 | 131.4 | 110.95 | -15.559
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 28.641 | 135.5 | 10.333 | 25 | 161.42 | 10.167 | 106.86 | 136.42 | 27.663
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 23.949 | 118.51 | 10.5 | 25 | 173.58 | 10.167 | 94.561 | 148.58 | 57.126
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 24.803 | 156.77 | 10.333 | 25 | 174.86 | 10.167 | 131.97 | 149.86 | 13.554
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 22.398 | 131.45 | 10.167 | 25 | 172.98 | 10.167 | 109.05 | 147.98 | 35.701
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 22.975 | 147.64 | 10.167 | 25 | 173.84 | 10.167 | 124.67 | 148.84 | 19.386
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 22.705 | 93.916 | 10.667 | 25 | 150.18 | 10.167 | 71.211 | 125.18 | 75.78
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 354 | 0 | 30 | Max |  |  | 24.791 | 172.95 | 10 | 25 | 146.54 | 10.167 | 148.16 | 121.54 | -17.968
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 27.64 | 175.46 | 10.167 | 25 | 177.53 | 10.167 | 147.82 | 152.53 | 3.1841
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 31.892 | 357.16 | 10 | 25 | 175.56 | 10.167 | 325.27 | 150.56 | -53.712
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.04109 | 5.5428 | 10 | 0 | 4.5785 | 10.167 | 5.5839 | 4.5785 | -18.006
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.099232 | 8.4143 | 9.1667 | 0 | 4.7163 | 10.167 | 8.5136 | 4.7163 | -44.603
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.0036053 | 4.9306 | 8.8333 | 0 | 4.5268 | 10.167 | 4.927 | 4.5268 | -8.1241
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.0006272 | 5.9794 | 6.3333 | 0 | 4.6571 | 10.167 | 5.98 | 4.6571 | -22.122
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | 0.0038998 | 2.9156 | 9.8333 | 0 | 4.1378 | 10.167 | 2.9117 | 4.1378 | 42.111
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.0025622 | 3.5554 | 9.8333 | 0 | 4.286 | 10.167 | 3.5529 | 4.286 | 20.635
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | 0.0002463 | 1.9313 | 9.8333 | 0 | 3.856 | 10.167 | 1.931 | 3.856 | 99.685
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.00043479 | 6.0247 | 4.8333 | 0 | 4.2945 | 10.167 | 6.0252 | 4.2945 | -28.724
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.048777 | 3.8865 | 10 | 0 | 4.363 | 10.167 | 3.8377 | 4.363 | 13.688
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.055748 | 3.3108 | 10.333 | 0 | 4.3027 | 10.167 | 3.2551 | 4.3027 | 32.186
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max |  |  | -0.19385 | 2.2696 | 9.5 | 0 | 4.3574 | 10.167 | 2.4635 | 4.3574 | 76.878
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.046195 | 4.7458 | 9.6667 | 0 | 4.3514 | 10.167 | 4.6996 | 4.3514 | -7.4083
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.035853 | 2.591 | 10.167 | 0 | 3.6042 | 10.167 | 2.5552 | 3.6042 | 41.057
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | 0.069214 | 8.7027 | 6 | 0 | 3.4969 | 10.167 | 8.6335 | 3.4969 | -59.496
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.088169 | 6.2297 | 9.6667 | 0 | 4.4273 | 10.167 | 6.1416 | 4.4273 | -27.913
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max |  |  | 0.14233 | 13.065 | 10 | 0 | 4.3021 | 10.167 | 12.923 | 4.3021 | -66.709
Experiment | ICFMP3_Test_9 | 1
Model | ICFMP3_Test_9 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 28.72 | 232.71 | 23.167 | 27 | 267.56 | 23 | 203.99 | 240.56 | 17.929
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 | 0.9 | 22.5 | 3.82 | 1.0185 | 3.6667 | -2.92 | -2.8015 | -4.0589
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 27.4 | 262 | 23.167 | 27 | 267.56 | 23 | 234.6 | 240.56 | 2.5422
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.155 | 22.833 | 0.20269 | 0.16076 | 12.167 | -0.054 | -0.041929 | -22.354
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.0313 | 13 | 0 | 0.026939 | 13.833 | 0.0313 | 0.026939 | -13.932
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 117 | 19.833 | 0 | 138.81 | 10.667 | 117 | 138.81 | 18.643
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 | -1.96 | 24.667 | 0 | -2.0986 | 23.5 | -1.96 | -2.0986 | 7.0704
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 27.5 | 255 | 23.5 | 27 | 245.02 | 23.5 | 227.5 | 218.02 | -4.1648
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 28.6 | 249 | 24 | 27 | 246.21 | 23.333 | 220.4 | 219.21 | -0.53902
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 27.4 | 222 | 23.5 | 27 | 183.22 | 23.333 | 194.6 | 156.22 | -19.724
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 27.6 | 194 | 23.667 | 27 | 247.94 | 23.333 | 166.4 | 220.94 | 32.779
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 23.1 | 136 | 23.5 | 27 | 210.61 | 23.333 | 112.9 | 183.61 | 62.631
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 24.1 | 202 | 23.167 | 27 | 226.78 | 23.167 | 177.9 | 199.78 | 12.3
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max |  |  | 21.9 | 110 | 23.833 | 27 | 174.9 | 23.333 | 88.1 | 147.9 | 67.879
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 139 | 325 | 346 | 0 | 30 | Max |  |  | 22.1 | 157 | 23.333 | 27 | 214.59 | 23.333 | 134.9 | 187.59 | 39.055
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 21.9 | 75 | 23.833 | 27 | 165.73 | 23.333 | 53.1 | 138.73 | 161.26
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 23.2 | 145 | 22.333 | 27 | 161.56 | 23.333 | 121.8 | 134.56 | 10.479
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 166 | 325 | 348 | 0 | 30 | Max |  |  | 27.4 | 231 | 21.667 | 27 | 217.55 | 23.333 | 203.6 | 190.55 | -6.4077
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 38.1 | 328 | 22 | 27 | 221.23 | 23.167 | 289.9 | 194.23 | -33.002
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.0343 | 6.55 | 21.167 | 0 | 4.7498 | 22.833 | 6.5843 | 4.7498 | -27.862
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.0279 | 9.03 | 23 | 0 | 4.9162 | 22.833 | 9.0579 | 4.9162 | -45.725
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.02 | 5.06 | 20.5 | 0 | 4.7243 | 22.833 | 5.08 | 4.7243 | -7.0029
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.0423 | 6.33 | 22.667 | 0 | 5.3196 | 22.833 | 6.3723 | 5.3196 | -16.52
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.0237 | 4.27 | 22.833 | 0 | 4.6838 | 22.833 | 4.2937 | 4.6838 | 9.0858
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | -0.0281 | 5.23 | 22.833 | 0 | 4.8549 | 22.833 | 5.2581 | 4.8549 | -7.6691
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.0115 | 2.72 | 22.833 | 0 | 4.338 | 22.833 | 2.7315 | 4.338 | 58.815
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.0547 | 5.1 | 3.6667 | 0 | 5.2786 | 22.833 | 5.1547 | 5.2786 | 2.4035
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.043344 | 3.4596 | 23 | 0 | 4.2672 | 23 | 3.4162 | 4.2672 | 24.911
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.06777 | 4.2722 | 23 | 0 | 4.8213 | 22.833 | 4.2045 | 4.8213 | 14.671
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | 0.0337 | 2.4517 | 23.667 | 0 | 3.4245 | 23 | 2.418 | 3.4245 | 41.623
Compare | Short Wall 2 Flux | Surface Flux | 1 | 17 | 325 | 369 | [14 empty] | No experimental measureme
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.025656 | 1.9373 | 23.333 | 0 | 3.0359 | 23 | 1.9116 | 3.0359 | 58.815
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max |  |  | 0.065967 | 3.9525 | 22.667 | 0 | 2.9301 | 23 | 3.8865 | 2.9301 | -24.608
Compare | Ceiling 1 Flux | Surface Flux | 1 | 31 | 325 | 371 | 0 | 30 | Max |  |  | 0.13735 | 5.5879 | 22 | 0 | 4.4642 | 23 | 5.4505 | 4.4642 | -18.097
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max |  |  | 0.29677 | 9.7071 | 21.167 | 0 | 4.5899 | 22.833 | 9.4103 | 4.5899 | -51.225
Experiment | ICFMP3_Test_10 | 1
Model | ICFMP3_Test_10 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 23.72 | 221.55 | 13.833 | 27 | 248.01 | 13.667 | 197.83 | 221.01 | 11.718
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.59 | 17.333 | 3.82 | 0.018695 | 13.667 | -3.23 | -3.8013
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 22.535 | 240.08 | 13.333 | 27 | 248.01 | 13.667 | 217.55 | 221.01 | 1.5922
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.20938 | 0.13014 | 14.167 | 0.20262 | 0.14325 | 13.667 | -0.079243 | -0.059369 | -25.08
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.046545 | 14.167 | 0 | 0.03473 | 13.667 | 0.046545 | 0.03473 | -25.385
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 70.747 | 7.3333 | 0 | 176.72 | 13.833 | 70.747 | 176.72 | 149.79
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 49.326 | 1.8333 | 0 | 45.703 | 3 | 49.326 | 45.703 | -7.3442
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 26.524 | 170.28 | 14 | 27 | 188.74 | 13.667 | 143.76 | 161.74 | 12.507
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 26.801 | 159.25 | 13.833 | 27 | 190.53 | 13.667 | 132.45 | 163.53 | 23.469
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 25.986 | 176.44 | 13.833 | 27 | 155.55 | 13.667 | 150.46 | 128.55 | -14.559
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 26.698 | 175 | 13.833 | 27 | 175.87 | 13.667 | 148.3 | 148.87 | 0.38491
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 21.931 | 115.9 | 14 | 27 | 176.75 | 13.833 | 93.967 | 149.75 | 59.36
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 22.8 | 185.49 | 13.667 | 27 | 178.39 | 13.667 | 162.69 | 151.39 | -6.9488
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max |  |  | 21.049 | 126.73 | 14 | 27 | 176.44 | 13.833 | 105.68 | 149.44 | 41.407
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 21.121 | 138.31 | 13.667 | 27 | 176.84 | 13.833 | 117.19 | 149.84 | 27.855
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 21.524 | 92.572 | 14 | 27 | 156.65 | 13.667 | 71.047 | 129.65 | 82.487
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max |  |  | 22.349 | 180.23 | 13.833 | 27 | 153.74 | 13.667 | 157.89 | 126.74 | -19.729
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 24.76 | 162.62 | 13.833 | 27 | 179.96 | 13.833 | 137.86 | 152.96 | 10.952
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 24.787 | 245.9 | 3.3333 | 27 | 179.55 | 13.667 | 221.12 | 152.55 | -31.007
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.0039613 | 4.9012 | 13.667 | 0 | 4.0796 | 13.667 | 4.9052 | 4.0796 | -16.831
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | 0.049931 | 6.7647 | 12.833 | 0 | 4.2052 | 13.667 | 6.7148 | 4.2052 | -37.375
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.061618 | 4.2995 | 13.833 | 0 | 4.0372 | 13.667 | 4.3612 | 4.0372 | -7.4289
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | 0.14877 | 6.3522 | 13.5 | 0 | 4.2012 | 13.667 | 6.2034 | 4.2012 | -32.276
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.011929 | 2.6779 | 13.667 | 0 | 3.8373 | 13.667 | 2.6898 | 3.8373 | 42.657
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | -0.0063498 | 2.9066 | 12.833 | 0 | 3.9729 | 13.667 | 2.913 | 3.9729 | 36.387
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.0041871 | 1.9236 | 13.667 | 0 | 3.5834 | 13.667 | 1.9278 | 3.5834 | 85.88
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.0050241 | 5.419 | 6.1667 | 0 | 3.9598 | 13.667 | 5.4241 | 3.9598 | -26.995
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.028061 | 3.3739 | 13.667 | 0 | 3.9315 | 13.667 | 3.3458 | 3.9315 | 17.506
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.033425 | 3.515 | 13.667 | 0 | 3.9295 | 13.667 | 3.4816 | 3.9295 | 12.864
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | 0.021902 | 3.1444 | 13.667 | 0 | 3.9301 | 13.667 | 3.1225 | 3.9301 | 25.861
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.026702 | 3.9061 | 13.667 | 0 | 3.9227 | 13.667 | 3.8794 | 3.9227 | 1.1159
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.018772 | 2.2937 | 13.5 | 0 | 3.3052 | 13.667 | 2.2749 | 3.3052 | 45.288
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | 0.1174 | 8.0101 | 6.5 | 0 | 3.2236 | 13.667 | 7.8927 | 3.2236 | -59.158
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.026277 | 4.8178 | 13.833 | 0 | 3.9828 | 13.667 | 4.7915 | 3.9828 | -16.878
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372
Experiment | ICFMP3_Test_13 | 1
Model | ICFMP3_Test_13 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 32.57 | 323.06 | 5.8333 | 31 | 341.87 | 6 | 290.49 | 310.87 | 7.0164
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.84 | 7.5 | 3.82 | 0.016898 | 6 | -2.98 | -3.8031
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 33.502 | 363.92 | 5.8333 | 31 | 341.87 | 6 | 330.42 | 310.87 | -5.9165
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.20907 | 0.10848 | 6.1667 | 0.20243 | 0.092259 | 6.1667 | -0.10059 | -0.11017 | 9.5264
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.060082 | 6.1667 | 0 | 0.064363 | 6.1667 | 0.060082 | 0.064363 | 7.1254
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 223.51 | 5.1667 | 0 | 479.93 | 28 | 223.51 | 479.93 | 114.72
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 231.54 | 2 | 0 | 335.6 | 2.8333 | 231.54 | 335.6 | 44.943
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 33.531 | 219.41 | 6.1667 | 31 | 195.68 | 6 | 185.88 | 164.68 | -11.404
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 34.486 | 207.88 | 4.5 | 31 | 199.37 | 6 | 173.4 | 168.37 | -2.8974
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 33.631 | 177.01 | 5.6667 | 31 | 173.65 | 6 | 143.38 | 142.65 | -0.50947
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 34.148 | 167.46 | 6 | 31 | 194.96 | 6 | 133.32 | 163.96 | 22.986
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 28.645 | 139.01 | 6.1667 | 31 | 225.7 | 6 | 110.36 | 194.7 | 76.411
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 29.757 | 229.19 | 6 | 31 | 228.84 | 6 | 199.43 | 197.84 | -0.79612
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 27.158 | 153.74 | 6 | 31 | 224.88 | 6 | 126.58 | 193.88 | 53.162
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 139 | 325 | 346 | 0 | 30 | Max |  |  | 27.369 | 172.28 | 6 | 31 | 226.3 | 6 | 144.91 | 195.3 | 34.772
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 27.421 | 116.63 | 6.1667 | 31 | 197 | 6 | 89.208 | 166 | 86.083
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 28.735 | 177.5 | 5.8333 | 31 | 191.85 | 6 | 148.76 | 160.85 | 8.1248
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 177 | 325 | 351 | 0 | 30 | Max |  |  | 33.718 | 352.99 | 5.8333 | 31 | 227.23 | 6 | 319.28 | 196.23 | -38.54
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max |  |  | 35.428 | 533.5 | 5.6667 | 31 | 227.62 | 6 | 498.07 | 196.62 | -60.523
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.010396 | 8.2543 | 5.6667 | 0 | 8.4281 | 6 | 8.2647 | 8.4281 | 1.9775
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | 0.033792 | 11.255 | 4.3333 | 0 | 8.6912 | 6 | 11.221 | 8.6912 | -22.546
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.043592 | 7.3282 | 5.6667 | 0 | 8.0455 | 6 | 7.2846 | 8.0455 | 10.445
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.033618 | 12.142 | 5.8333 | 0 | 8.5561 | 6 | 12.176 | 8.5561 | -29.729
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | 0.0014911 | 4.7739 | 4.6667 | 0 | 7.6938 | 6 | 4.7724 | 7.6938 | 61.213
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.0046788 | 6.5843 | 4.3333 | 0 | 7.9837 | 6 | 6.5796 | 7.9837 | 21.341
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.0018226 | 2.8955 | 4.6667 | 0 | 7.1425 | 6 | 2.8973 | 7.1425 | 146.52
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.00014493 | 10.063 | 3.5 | 0 | 7.9967 | 6 | 10.063 | 7.9967 | -20.533
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | [14 empty] | No experimental measureme
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | [14 empty] | No experimental measureme
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | [14 empty] | No experimental measureme
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 369 | [14 empty] | No experimental measureme
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | [14 empty] | No experimental measureme
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | [14 empty] | No experimental measureme
Compare | Ceiling 1 Flux | Surface Flux | 1 | 36 | 325 | 374 | [14 empty] | No experimental measureme
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | [14 empty] | No experimental measureme
Experiment | ICFMP3_Test_14 | 1
Model | ICFMP3_Test_14 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 26.26 | 234.49 | 23 | 28 | 269.62 | 23 | 208.23 | 241.62 | 16.037
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 | 0.91 | 22.5 | 3.82 | 1.0142 | 3.6667 | -2.91 | -2.8058 | -3.5801
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 26.2 | 267 | 22 | 28 | 269.62 | 23 | 240.8 | 241.62 | 0.34177
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.154 | 12.667 | 0.2025 | 0.16048 | 12 | -0.055 | -0.042021 | -23.598
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.0322 | 14.5 | 0 | 0.027097 | 13.833 | 0.0322 | 0.027097 | -15.848
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 91.3 | 27 | 0 | 139.24 | 10.667 | 91.3 | 139.24 | 52.512
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 | -2.05 | 25.333 | 0 | -2.1193 | 23.667 | -2.05 | -2.1193 | 3.3785
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 28 | 227 | 23.333 | 28 | 234.71 | 23.667 | 199 | 206.71 | 3.8734
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 28.7 | 207 | 23.333 | 28 | 235.77 | 23.667 | 178.3 | 207.77 | 16.528
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 27.8 | 199 | 23.833 | 28 | 172.81 | 23.5 | 171.2 | 144.81 | -15.417
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 28.1 | 298 | 21.333 | 28 | 289.9 | 23.167 | 269.9 | 261.9 | -2.9655
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 23.6 | 138 | 23.667 | 28 | 212.23 | 23.333 | 114.4 | 184.23 | 61.038
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 24.3 | 279 | 23.167 | 28 | 249.9 | 23.167 | 254.7 | 221.9 | -12.879
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 343 | 0 | 30 | Max |  |  | 22.2 | 109 | 24 | 28 | 176.96 | 23.333 | 86.8 | 148.96 | 71.613
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 22.4 | 170 | 23.5 | 28 | 216.92 | 23.5 | 147.6 | 188.92 | 27.995
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 22.5 | 74.7 | 24 | 28 | 168.67 | 23.5 | 52.2 | 140.67 | 169.48
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 23.2 | 127 | 23.5 | 28 | 164.55 | 23.5 | 103.8 | 136.55 | 31.554
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 26.3 | 184 | 23.5 | 28 | 220.22 | 23.333 | 157.7 | 192.22 | 21.89
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max |  |  | 29.2 | 381 | 22.667 | 28 | 228.39 | 23.167 | 351.8 | 200.39 | -43.039
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | 0.0107 | 3.83 | 22 | 0 | 4.2643 | 23 | 3.8193 | 4.2643 | 11.652
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.0132 | 6.06 | 20.833 | 0 | 4.4282 | 23 | 6.0732 | 4.4282 | -27.087
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.00639 | 3.47 | 22.167 | 0 | 4.3476 | 23 | 3.4636 | 4.3476 | 25.522
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.001 | 10.9 | 22.333 | 0 | 7.2528 | 23 | 10.901 | 7.2528 | -33.467
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | 0.000229 | 2.84 | 23.167 | 0 | 4.1451 | 23 | 2.8398 | 4.1451 | 45.967
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.00234 | 3.32 | 23.333 | 0 | 4.3141 | 23 | 3.3177 | 4.3141 | 30.036 | No experimental measureme
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | 0.00118 | 2.12 | 23.333 | 0 | 3.8779 | 23 | 2.1188 | 3.8779 | 83.024
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.00135 | 10.5 | 2.5 | 0 | 7.2915 | 23 | 10.501 | 7.2915 | -30.566
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.041597 | 3.5411 | 23.667 | 0 | 4.3033 | 23 | 3.4995 | 4.3033 | 22.97
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.04999 | 8.1535 | 23 | 0 | 5.6733 | 23 | 8.1035 | 5.6733 | -29.99
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | 0.03291 | 2.3844 | 22.833 | 0 | 3.5088 | 23 | 2.3515 | 3.5088 | 49.214
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.04122 | 4.512 | 23 | 0 | 4.4613 | 23 | 4.4708 | 4.4613 | -0.21263
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.03008 | 1.9227 | 23.5 | 0 | 3.0998 | 23 | 1.8926 | 3.0998 | 63.788
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max |  |  | 0.038874 | 3.0079 | 23 | 0 | 2.9942 | 23 | 2.969 | 2.9942 | 0.85055
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.046968 | 4.7415 | 23.333 | 0 | 4.5419 | 23 | 4.6945 | 4.5419 | -3.2516
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | 0 | 30 | Max |  |  | 0.094376 | 9.0879 | 19.5 | 0 | 4.8348 | 23 | 8.9935 | 4.8348 | -46.241
Experiment | ICFMP3_Test_15 | 1
Model | ICFMP3_Test_15 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 22.83 | 233.4 | 23.333 | 18 | 259.95 | 23 | 210.57 | 241.95 | 14.9
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 | 0.93 | 18.333 | 3.82 | 1.0307 | 3.6667 | -2.89 | -2.7893 | -3.4837
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 22.185 | 265.85 | 22.667 | 18 | 259.95 | 23 | 243.66 | 241.95 | -0.70545
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.20938 | 0.15774 | 23.5 | 0.20321 | 0.16124 | 12.5 | -0.051638 | -0.041969 | -18.725
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.031216 | 16 | 0 | 0.026688 | 14 | 0.031216 | 0.026688 | -14.504
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 122.72 | 29.667 | 0 | 139.52 | 10.833 | 122.72 | 139.52 | 13.69
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 | -2.3509 | 25.667 | 0 | -2.1996 | 23.667 | -2.3509 | -2.1996 | -6.4345
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 31.879 | 447.45 | 9.5 | 18 | 225.01 | 23.667 | 415.57 | 207.01 | -50.186
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 25.862 | 269.23 | 27.667 | 18 | 226.74 | 23.5 | 243.37 | 208.74 | -14.231
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 25.101 | 694.51 | 23.5 | 18 | 172.81 | 23.5 | 669.41 | 154.81 | -76.873
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 25.541 | 186.6 | 24.333 | 18 | 281.34 | 23.167 | 161.06 | 263.34 | 63.508
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 125 | 325 | 340 | 0 | 30 | Max |  |  | 22.832 | 242.49 | 23.333 | 18 | 201.29 | 23.333 | 219.66 | 183.29 | -16.556
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 124 | 325 | 341 | 0 | 30 | Max |  |  | 22.819 | 228.27 | 23 | 18 | 205.59 | 23.333 | 205.45 | 187.59 | -8.6951
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 343 | 0 | 30 | Max |  |  | 19.193 | 115.47 | 21.833 | 18 | 162.87 | 23.333 | 96.276 | 144.87 | 50.475
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 18.981 | 170.43 | 23.667 | 18 | 205.21 | 23.5 | 151.44 | 187.21 | 23.619
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 19.877 | 72.175 | 24.167 | 18 | 154.56 | 23.5 | 52.299 | 136.56 | 161.12
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 21.894 | 153.48 | 24.5 | 18 | 150.36 | 23.5 | 131.58 | 132.36 | 0.59248
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 23.995 | 180.86 | 23.5 | 18 | 208.75 | 23.333 | 156.87 | 190.75 | 21.602
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 25.893 | 313.05 | 23.333 | 18 | 204.12 | 23.333 | 287.15 | 186.12 | -35.184
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.55793 | 57.163 | 2.5 | 0 | 4.0022 | 23 | 57.721 | 4.0022 | -93.066
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | 0.0073127 | 20.88 | 4 | 0 | 4.161 | 23 | 20.872 | 4.161 | -80.065
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.43985 | 23.504 | 20.5 | 0 | 4.0277 | 23 | 23.944 | 4.0277 | -83.179
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.039012 | 5.085 | 22.167 | 0 | 7.0182 | 23 | 5.124 | 7.0182 | 36.969
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.60676 | 45.88 | 3.1667 | 0 | 3.8823 | 23 | 46.487 | 3.8823 | -91.649
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | [14 empty] | No experimental measureme
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.26462 | 18.022 | 15.333 | 0 | 3.6167 | 23 | 18.287 | 3.6167 | -80.223
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.085315 | 3.6452 | 23 | 0 | 7.0608 | 23 | 3.7305 | 7.0608 | 89.271
Compare | Long Wall 1 Flux | Surface Flux | 1 | 8 | 325 | 363 | 0 | 30 | Max |  |  | 0.023839 | 3.659 | 23 | 0 | 4.0693 | 23 | 3.6352 | 4.0693 | 11.944
Compare | Long Wall 2 Flux | Surface Flux | 1 | 10 | 325 | 364 | 0 | 30 | Max |  |  | 0.1473 | 7.6105 | 3.3333 | 0 | 4.2069 | 23 | 7.4632 | 4.2069 | -43.631
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | 0.012182 | 2.6224 | 21.833 | 0 | 3.2579 | 23 | 2.6102 | 3.2579 | 24.814
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.020593 | 4.6752 | 22.667 | 0 | 4.1944 | 23 | 4.6546 | 4.1944 | -9.8865
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | -0.0044573 | 1.9441 | 23.167 | 0 | 2.8519 | 23 | 1.9485 | 2.8519 | 46.362
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max |  |  | 0.053569 | 5.2852 | 23.333 | 0 | 2.7506 | 23 | 5.2316 | 2.7506 | -47.424
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372
Experiment | ICFMP3_Test_16 | 1
Model | ICFMP3_Test_16 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 21.42 | 289.86 | 6.3333 | 26 | 315.68 | 6.3333 | 268.44 | 289.68 | 7.9139
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.53 | 23.833 | 3.82 | 0.015784 | 6.3333 | -3.29 | -3.8042
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 20.726 | 298.39 | 6.3333 | 26 | 315.68 | 6.3333 | 277.66 | 289.68 | 4.3302
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.20943 | 0.11799 | 6.8333 | 0.20342 | 0.12878 | 6.3333 | -0.091445 | -0.074639 | -18.379
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.055209 | 6.8333 | 0 | 0.043607 | 6.3333 | 0.055209 | 0.043607 | -21.015
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 139.07 | 5 | 0 | 204.2 | 6.8333 | 139.07 | 204.2 | 46.832
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 80.58 | 1.6667 | 0 | 308.54 | 3 | 80.58 | 308.54 | 282.91
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 23.871 | 184.32 | 6.5 | 26 | 191.29 | 6.3333 | 160.45 | 165.29 | 3.0167
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 23.447 | 179.33 | 5.6667 | 26 | 195.63 | 6.3333 | 155.88 | 169.63 | 8.8196
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 23.77 | 192.24 | 6.6667 | 26 | 173.4 | 6.3333 | 168.47 | 147.4 | -12.509
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 24.543 | 193.69 | 6.1667 | 26 | 175.79 | 6.3333 | 169.15 | 149.79 | -11.441
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 19.741 | 126.59 | 6.5 | 26 | 201.1 | 6.3333 | 106.85 | 175.1 | 63.874
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 20.9 | 238.03 | 6.1667 | 26 | 205.81 | 6.3333 | 217.13 | 179.81 | -17.188
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 19.042 | 142.26 | 6.3333 | 26 | 200.44 | 6.3333 | 123.22 | 174.44 | 41.565
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 18.949 | 160.11 | 6.5 | 26 | 201.28 | 6.3333 | 141.16 | 175.28 | 24.169
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 19.962 | 99.975 | 6.6667 | 26 | 173.78 | 6.3333 | 80.012 | 147.78 | 84.692
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 20.515 | 166.38 | 6.5 | 26 | 169.28 | 6.3333 | 145.87 | 143.28 | -1.7709
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 177 | 325 | 351 | 0 | 30 | Max |  |  | 22.806 | 306.49 | 6.5 | 26 | 203.65 | 6.3333 | 283.68 | 177.65 | -37.378
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max |  |  | 23.398 | 464.78 | 6.3333 | 26 | 205.19 | 6.3333 | 441.38 | 179.19 | -59.402
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.32311 | 8.0431 | 6.1667 | 0 | 7.1471 | 6.3333 | 8.3662 | 7.1471 | -14.572
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.41521 | 11.25 | 6.1667 | 0 | 7.3846 | 6.3333 | 11.666 | 7.3846 | -36.698
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.078991 | 6.0559 | 5.5 | 0 | 6.7754 | 6.3333 | 6.1349 | 6.7754 | 10.441
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.014551 | 12.214 | 5.3333 | 0 | 7.3336 | 6.3333 | 12.228 | 7.3336 | -40.028
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.066182 | 4.0505 | 6.1667 | 0 | 6.5385 | 6.3333 | 4.1167 | 6.5385 | 58.828
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | -0.093243 | 4.7387 | 6.1667 | 0 | 6.8064 | 6.3333 | 4.832 | 6.8064 | 40.862
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.02931 | 2.7286 | 6.3333 | 0 | 6.0351 | 6.3333 | 2.7579 | 6.0351 | 118.83
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.17507 | 11.788 | 4 | 0 | 6.7876 | 6.3333 | 11.963 | 6.7876 | -43.264
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | [14 empty] | No experimental measureme
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | [14 empty] | No experimental measureme
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | [14 empty] | No experimental measureme
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | [14 empty] | No experimental measureme
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | [14 empty] | No experimental measureme
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | [14 empty] | No experimental measureme
Compare | Ceiling 1 Flux | Surface Flux | 1 | 36 | 325 | 374 | [14 empty] | No experimental measureme
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | [14 empty] | No experimental measureme
Experiment | ICFMP3_Test_17 | 1
Model | ICFMP3_Test_17 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 25.7 | 161.03 | 4.5 | 27 | 170.19 | 4.5 | 135.33 | 143.19 | 5.8102
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.69 | 5.6667 | 3.82 | 0.4899 | 4.5 | -3.13 | -3.3301
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 24.552 | 180.4 | 4.5 | 27 | 170.19 | 4.5 | 155.85 | 143.19 | -8.122
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.20927 | 0.17584 | 4.8333 | 0.20427 | 0.17319 | 4.6667 | -0.033432 | -0.031083 | -7.0259
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.021633 | 4.8333 | 0 | 0.016648 | 4.6667 | 0.021633 | 0.016648 | -23.044
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 353.09 | 4.6667 | 0 | 1589.9 | 14.833 | 353.09 | 1589.9 | 350.28
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 194.86 | 3.3333 | 0 | 137.45 | 3 | 194.86 | 137.45 | -29.465
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | [14 empty] | No experimental measureme
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | [14 empty] | No experimental measureme
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | [14 empty] | No experimental measureme
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | [14 empty] | No experimental measureme
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 23.635 | 62.641 | 4.8333 | 27 | 79.895 | 4.6667 | 39.006 | 52.895 | 35.609
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 23.952 | 106.01 | 4.5 | 27 | 92.248 | 4.5 | 82.059 | 65.248 | -20.487
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max |  |  | 22.064 | 78.542 | 4.6667 | 27 | 78.569 | 4.6667 | 56.478 | 51.569 | -8.6931
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 22.412 | 83.436 | 4.6667 | 27 | 81.038 | 4.6667 | 61.024 | 54.038 | -11.448
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 22.094 | 46.53 | 5 | 27 | 61.11 | 4.6667 | 24.436 | 34.11 | 39.589
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 22.123 | 74.042 | 4.5 | 27 | 59.526 | 4.6667 | 51.919 | 32.526 | -37.353
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 26.411 | 95.054 | 4.6667 | 27 | 84.735 | 4.6667 | 68.643 | 57.735 | -15.891
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 27.097 | 256.89 | 4.1667 | 27 | 91.352 | 4.5 | 229.79 | 64.352 | -71.995
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.020958 | 2.3411 | 4.3333 | 0 | 2.5837 | 4.5 | 2.3621 | 2.5837 | 9.3833
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.12546 | 3.1608 | 4.3333 | 0 | 2.6865 | 4.5 | 3.2863 | 2.6865 | -18.25
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.0044246 | 1.8564 | 4.6667 | 0 | 2.4061 | 4.5 | 1.852 | 2.4061 | 29.919
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.0043904 | 3.0618 | 4.1667 | 0 | 2.6604 | 4.5 | 3.0662 | 2.6604 | -13.234
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.0016058 | 1.2974 | 4.3333 | 0 | 2.0804 | 4.5 | 1.299 | 2.0804 | 60.158
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.010694 | 1.5322 | 4.1667 | 0 | 2.2011 | 4.5 | 1.5215 | 2.2011 | 44.666
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | 0.0002463 | 0.88156 | 4.5 | 0 | 1.8561 | 4.5 | 0.88131 | 1.8561 | 110.61
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | 0.0013527 | 2.4177 | 2.6667 | 0 | 2.2961 | 3 | 2.4164 | 2.2961 | -4.9785
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.0032924 | 1.4651 | 4.5 | 0 | 2.1086 | 4.5 | 1.4618 | 2.1086 | 44.244
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.0014042 | 0.93041 | 4.5 | 0 | 2.2775 | 4.5 | 0.92901 | 2.2775 | 145.15
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | 0.0066798 | 1.5661 | 4.3333 | 0 | 2.1062 | 4.5 | 1.5595 | 2.1062 | 35.06
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.010047 | 1.9091 | 4.3333 | 0 | 2.0973 | 4.5 | 1.899 | 2.0973 | 10.443
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.00831 | 0.86458 | 4.5 | 0 | 1.3776 | 4.5 | 0.85627 | 1.3776 | 60.881
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max |  |  | 0.011907 | 1.511 | 4.1667 | 0 | 1.3235 | 4.5 | 1.4991 | 1.3235 | -11.714
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | [14 empty] | No experimental measureme
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | [14 empty] | No experimental measureme
Experiment | ICFMP3_Test_18 | 1
Model | ICFMP3_Test_18 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 24.53 | 217.96 | 23.167 | 27 | 269.79 | 23 | 193.43 | 242.79 | 25.517
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 | 0.91 | 16.5 | 3.82 | 1.0128 | 3.6667 | -2.91 | -2.8072 | -3.533
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 24.308 | 259.32 | 22.5 | 27 | 269.79 | 23 | 235.01 | 242.79 | 3.3097
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.20938 | 0.15865 | 23 | 0.20427 | 0.16045 | 12.667 | -0.050739 | -0.043821 | -13.634
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.030642 | 22.833 | 0 | 0.027184 | 13.667 | 0.030642 | 0.027184 | -11.285
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 110.18 | 19.833 | 0 | 139.7 | 10.667 | 110.18 | 139.7 | 26.79
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 | -2.0059 | 26 | 0 | -2.1449 | 23.667 | -2.0059 | -2.1449 | 6.93
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 26.493 | 262.19 | 23.333 | 27 | 254.05 | 23.333 | 235.69 | 227.05 | -3.6649
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 26.829 | 244.04 | 23.5 | 27 | 248.5 | 23.5 | 217.21 | 221.5 | 1.9761
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 26.126 | 257.62 | 23.167 | 27 | 215.15 | 23.167 | 231.5 | 188.15 | -18.726
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 25.476 | 134.75 | 25.333 | 27 | 229.84 | 23.667 | 109.28 | 202.84 | 85.624 | No experimental measureme
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 121 | 325 | 338 | 0 | 30 | Max |  |  | 22.884 | 141.05 | 23.833 | 27 | 211.63 | 23.333 | 118.16 | 184.63 | 56.248
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 342 | 0 | 30 | Max |  |  | 23.342 | 335.71 | 23.167 | 27 | 275.3 | 23 | 312.36 | 248.3 | -20.507
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 343 | 0 | 30 | Max |  |  | 20.158 | 114.17 | 23.167 | 27 | 181.22 | 23.333 | 94.013 | 154.22 | 64.043
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 20.404 | 173.3 | 23.667 | 27 | 217.34 | 23.333 | 152.9 | 190.34 | 24.491
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 20.907 | 70.477 | 24.667 | 27 | 168.32 | 23.5 | 49.57 | 141.32 | 185.09
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 20.792 | 127.39 | 23.333 | 27 | 164.25 | 23.5 | 106.6 | 137.25 | 28.76
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 25.428 | 170.33 | 23.5 | 27 | 219.93 | 23.333 | 144.9 | 192.93 | 33.144
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 25.189 | 275.3 | 22.667 | 27 | 220.63 | 23.333 | 250.11 | 193.63 | -22.58
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.00082501 | 7.6089 | 19.333 | 0 | 5.1401 | 23 | 7.6097 | 5.1401 | -32.454
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.0092045 | 7.8253 | 23.167 | 0 | 5.0065 | 23 | 7.8345 | 5.0065 | -36.096
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.0055719 | 8.7296 | 23.167 | 0 | 5.9157 | 23 | 8.7351 | 5.9157 | -32.277
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | 0.0077772 | 4.4573 | 23.5 | 0 | 4.4939 | 23 | 4.4495 | 4.4939 | 0.99739
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | 0.0032116 | 5.2374 | 22.167 | 0 | 5.1001 | 23 | 5.2342 | 5.1001 | -2.5628
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | [14 empty] | No experimental measureme
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.002266 | 5.1785 | 22.167 | 0 | 5.708 | 23 | 5.1808 | 5.708 | 10.177
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.0030918 | 2.843 | 23.167 | 0 | 4.3872 | 23 | 2.8461 | 4.3872 | 54.147
Compare | Long Wall 1 Flux | Surface Flux | 1 | 8 | 325 | 363 | 0 | 30 | Max |  |  | 0.030144 | 3.4342 | 23.5 | 0 | 4.2703 | 23 | 3.4041 | 4.2703 | 25.446
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 365 | [14 empty] | No experimental measureme
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | 0.010887 | 2.5935 | 23.167 | 0 | 3.5242 | 23 | 2.5826 | 3.5242 | 36.46
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.024988 | 4.6904 | 22.333 | 0 | 4.4936 | 23 | 4.6654 | 4.4936 | -3.6835
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.017531 | 1.807 | 23.333 | 0 | 3.1074 | 23 | 1.7895 | 3.1074 | 73.651
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max |  |  | 0.018953 | 3.0758 | 23.167 | 0 | 3.0031 | 23 | 3.0569 | 3.0031 | -1.7599
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.033724 | 4.5122 | 23 | 0 | 4.5494 | 23 | 4.4785 | 4.5494 | 1.583
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | [14 empty] | No experimental measureme
Experiment | ICFMP4_Test_1 | 1
Model | ICFMP4_Test_1 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 117 | 136 | 1 | 2 | 0 | 30 | Max |  |  | 19.085 | 719.23 | 22.833 | 20 | 622.31 | 22.667 | 700.14 | 602.31 | -13.974
Compare | HGL Height | HGL Height | 117 | 138 | 1 | 3 | 0 | 20 | Min |  |  | 5.7 | 1.5 | 12.5 | 5.7 | 0.62435 | 19.833 | -4.2 | -5.0756 | 20.849
Compare | Steel Heat Flux | Surface Temperature | 117 | 186 | 1 | 11 | 0 | 30 | Max |  |  | 0.04 | 27.22 | 21.5 | 0 | 36.532 | 22.667 | 27.18 | 36.532 | 34.409
Compare | Concrete Heat Flux | Surface Temperature | 117 | 187 | 1 | 13 | 0 | 30 | Max |  |  | 0.03952 | 46.594 | 19 | 0 | 37.269 | 22.667 | 46.555 | 37.269 | -19.945
Compare | Light Concrete Heat Flux | Surface Temperature | 117 | 188 | 1 | 15 | 0 | 30 | Max |  |  | 0 | 32.413 | 25 | 0 | 35.759 | 22.667 | 32.413 | 35.759 | 10.325
Compare | Steel Heat Temperature | Surface Flux | 117 | 156 | 1 | 10 | 0 | 30 | Max |  |  | 19.53 | 375.53 | 25.333 | 20 | 379.67 | 23 | 356 | 359.67 | 1.0314
Compare | Concrete Heat Temperature | Surface Flux | 117 | 155 | 1 | 12 | 0 | 30 | Max |  |  | 18.78 | 326.93 | 23.333 | 20 | 432.79 | 22.833 | 308.15 | 412.79 | 33.959
Compare | Light Concrete Heat Temperature | Surface Flux | 117 | 151 | 1 | 14 | 0 | 30 | Max |  |  | 17.89 | 507.04 | 23.167 | 20 | 534 | 22.833 | 489.15 | 514 | 5.08
Compare | M19 Temperature | Surface Temperature | 117 | 139 | 1 | 16 | 0 | 30 | Max |  |  | 19.15 | 614.89 | 23 | 20 | 566.19 | 22.667 | 595.74 | 546.19 | -8.3179
Compare | M20 Temperature | Surface Temperature | 117 | 140 | 1 | 17 | 0 | 30 | Max |  |  | 19.33 | 741 | 22.833 | 20 | 257.94 | 24.667 | 721.67 | 237.94 | -67.029
Experiment | ICFMP5_Test_4 | 1
Model | ICFMP5_Test_4 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 125 | 168 | 1 | 2 | 0 | 20 | Max |  |  | 18.652 | 169.46 | 19.5 | 20 | 191.59 | 19.833 | 150.81 | 171.59 | 13.78
Compare | HGL Height | HGL Height | 125 | 170 | 1 | 3 | 5 | 20 | Min |  |  | 5.6 | 1.2813 | 18.167 | 5.6 | 2.1588 | 19.833 | -4.3187 | -3.4412 | -20.318
Compare | Oxygen | Oxygen | 125 | 293 | 1 | 5 | 0 | 20 | Min |  |  | 0.20951 | 0.18622 | 19.833 | 0.2048 | 0.18512 | 19.833 | -0.023289 | -0.019683 | -15.485
Compare | Carbon Dioxide | Carbon Dioxide | 125 | 295 | 1 | 6 | 0 | 20 | Max |  |  | 0.00054078 | 0.013479 | 19.833 | 0 | 0.011777 | 19.833 | 0.012938 | 0.011777 | -8.9753
Compare | WS2 Flux | Cable Flux | 125 | 271 | 1 | 11 | 0 | 20 | Max |  |  | -0.01 | 2.9 | 18 | 0 | 1.62 | 19.833 | 2.91 | 1.62 | -44.332
Compare | WS 3 Flux | Cable Flux | 125 | 172 | 1 | 13 | 0 | 20 | Max |  |  | 0 | 96.68 | 19.833 | 0 | 2.1556 | 19.833 | 96.68 | 2.1556 | -97.77
Compare | WS 4 Flux | Cable Flux | 125 | 273 | 1 | 15 | 0 | 20 | Max |  |  | -0.01 | 5.74 | 15.5 | 0 | 2.1542 | 19.833 | 5.75 | 2.1542 | -62.536
Compare | TCO 1-3 Temperature | Cable Temperature | 125 | 199 | 1 | 18 | 0 | 20 | Max |  |  | 18.42 | 105.64 | 19.5 | 20 | 86.342 | 19.833 | 87.22 | 66.342 | -23.937
Compare | TCO 1-5 Temperature | Cable Temperature | 125 | 201 | 1 | 19 | 0 | 20 | Max |  |  | 18.77 | 128.52 | 19.333 | 20 | 107.23 | 19.833 | 109.75 | 87.23 | -20.519
Compare | TCO 1-7 Temperature | Cable Temperature | 125 | 203 | 1 | 20 | 0 | 20 | Max |  |  | 18.93 | 125.62 | 19.667 | 20 | 107.15 | 19.833 | 106.69 | 87.154 | -18.311
Compare | TCO 3-3 Temperature | Cable Temperature | 125 | 217 | 1 | 21 | 0 | 20 | Max |  |  | 18.5 | 130.18 | 19.5 | 20 | 104.9 | 19.833 | 111.68 | 84.905 | -23.975
Compare | TCO 3-5 Temperature | Cable Temperature | 125 | 219 | 1 | 22 | 0 | 20 | Max |  |  | 18.84 | 165.09 | 19.333 | 20 | 134.15 | 19.833 | 146.25 | 114.15 | -21.951
Compare | TCO 3-7 Temperature | Cable Temperature | 125 | 221 | 1 | 23 | 0 | 20 | Max |  |  | 19.01 | 159.26 | 19.5 | 20 | 133.13 | 19.833 | 140.25 | 113.13 | -19.335
Compare | TW 1-1 Temperature | Surface Temperature | 125 | 171 | 1 | 24 | 0 | 20 | Max |  |  | 18.73 | 74.63 | 19.833 | 20 | 56.563 | 19.833 | 55.9 | 36.563 | -34.592
Compare | TW 1-4 Temperature | Surface Temperature | 125 | 174 | 1 | 25 | 0 | 20 | Max |  |  | 18.88 | 106.23 | 19.833 | 20 | 56.217 | 19.833 | 87.35 | 36.217 | -58.538
Compare | TW 1-7 Temperature | Surface Temperature | 125 | 177 | 1 | 26 | 0 | 20 | Max |  |  | 18.76 | 104.92 | 19.667 | 20 | 56.927 | 19.833 | 86.16 | 36.927 | -57.141
Compare | TW 2-1 Temperature | Surface Temperature | 125 | 178 | 1 | 27 | 0 | 20 | Max |  |  | 17.73 | 22.14 | 19.833 | 20 | 43.912 | 19.833 | 4.41 | 23.912 | 442.23
Compare | TW 2-4 Temperature | Surface Temperature | 125 | 181 | 1 | 28 | 0 | 20 | Max |  |  | 19.15 | 87.17 | 19.833 | 20 | 54.71 | 19.833 | 68.02 | 34.71 | -48.971
Compare | TW 2-7 Temperature | Surface Temperature | 125 | 184 | 1 | 29 | 0 | 20 | Max |  |  | 18.99 | 90.8 | 19.833 | 20 | 56.686 | 19.833 | 71.81 | 36.686 | -48.912
Experiment | MV100A | 1
Model | MV100A | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Tree 1 HGL Temperature | HGL Temperature | 271 | 275 | 257 | 258 | 5 | 15 | Max |  |  | 23 | 282.39 | 14.667 | 23 | 260.43 | 14.833 | 259.39 | 237.43 | -8.4672
Compare | Tree 1 HGL Height | HGL Height | 271 | 273 | 257 | 259 | 5 | 15 | Min |  |  | 2.16 | 0.89 | 8.6667 | 2.16 | 0.84134 | 5 | -1.27 | -1.3187 | 3.8318
Compare | Tree 4 HGL Temperature | HGL Temperature | 271 | 279 | 257 | 264 | 5 | 15 | Max |  |  | 23 | 109.16 | 14.667 | 23 | 111.06 | 14.833 | 86.16 | 88.057 | 2.2017
Compare | Tree 4 HGL Height | HGL Height | 271 | 277 | 257 | 265 | 5 | 15 | Min |  |  | 2.44 | 1.27 | 14.5 | 2.44 | 1.2542 | 5 | -1.17 | -1.1858 | 1.347
Compare | Tree 5 HGL Temperature | HGL Temperature | 271 | 283 | 257 | 266 | 5 | 15 | Max |  |  | 23 | 100.28 | 14.333 | 23 | 111.06 | 14.833 | 77.28 | 88.057 | 13.945
Compare | Tree 5 HGL Height | HGL Height | 271 | 281 | 257 | 267 | 5 | 15 | Min |  |  | 2.44 | 1.15 | 14 | 2.44 | 1.2542 | 5 | -1.29 | -1.1858 | -8.0806
Compare | Tree 6 HGL Temperature | HGL Temperature | 271 | 287 | 257 | 268 | 5 | 15 | Max |  |  | 23 | 97.3 | 13.833 | 23 | 111.06 | 14.833 | 74.3 | 88.057 | 18.515
Compare | Tree 6 HGL Height | HGL Height | 271 | 285 | 257 | 269 | 5 | 15 | Min |  |  | 2.44 | 1.26 | 14.333 | 2.44 | 1.2542 | 5 | -1.18 | -1.1858 | 0.48813
Experiment | MV100O | 1
Model | MV100O | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Tree 1 HGL Temperature | HGL Temperature | 280 | 284 | 266 | 267 | 5 | 15 | Max |  |  | 21 | 333 | 14.333 | 20 | 355.65 | 14.667 | 312 | 335.65 | 7.5804
Compare | Tree 1 HGL Height | HGL Height | 280 | 282 | 266 | 268 | 5 | 15 | Min | Closed |  | 2.16 | 0.84 | 10 | 2.16 | 0.0036186 | 7.3333 | -1.32 | -2.1564
Compare | Tree 4 HGL Temperature | HGL Temperature | 280 | 288 | 266 | 273 | 5 | 15 | Max |  |  | 21 | 127.2 | 14.667 | 20 | 94.789 | 14.833 | 106.2 | 74.789 | -29.577
Compare | Tree 4 HGL Height | HGL Height | 280 | 286 | 266 | 274 | 5 | 15 | Min | Closed |  | 2.44 | 0.68 | 14.833 | 2.44 | 0.000244 | 6.8333 | -1.76 | -2.4398
Compare | Tree 5 HGL Temperature | HGL Temperature | 280 | 292 | 266 | 275 | 5 | 15 | Max |  |  | 21 | 120.33 | 14.667 | 20 | 94.789 | 14.833 | 99.33 | 74.789 | -24.706
Compare | Tree 5 HGL Height | HGL Height | 280 | 290 | 266 | 276 | 5 | 15 | Min | Closed |  | 2.44 | 0.52 | 14.833 | 2.44 | 0.000244 | 6.8333 | -1.92 | -2.4398
Compare | Tree 6 HGL Temperature | HGL Temperature | 280 | 296 | 266 | 277 | [5 empty] | 21 | [8 empty] | No experimental measureme
Compare | Tree 6 HGL Height | HGL Height | 280 | 294 | 266 | 278 | 5 | 15 | Min | Closed |  | 1.11 | 0.59 | 14.833 | 2.4398 | 0.000244 | 6.8333 | -0.52 | -2.4395
Experiment | MV100Z | 1
Model | MV100Z | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Tree 1 HGL Temperature | HGL Temperature | 331 | 335 | 313 | 314 | 5 | 15 | Max |  |  | 22 | 282 | 13 | 22 | 262.33 | 14.833 | 285.67 | 240.33 | -15.873 | Experimental Peak = 282
Compare | Tree 1 HGL Height | HGL Height | 331 | 333 | 313 | 315 | 5 | 15 | Min |  |  | 2.16 | 1 | 9.6667 | 2.16 | 0.83962 | 5.1667 | -1.34 | -1.3204 | -1.464 | Experimental Peak = 1.0
Compare | Tree 4 HGL Temperature | HGL Temperature | 331 | 339 | 313 | 320 | 5 | 15 | Max |  |  | 22 | 89.08 | 14 | 22 | 85.776 | 14.833 | 67.08 | 63.776 | -4.9253
Compare | Tree 4 HGL Height | HGL Height | 331 | 337 | 313 | 321 | 5 | 15 | Min |  |  | 2.44 | 1.27 | 12.167 | 2.44 | 0.92512 | 5.3333 | -1.17 | -1.5149 | 29.477
Compare | Tree 5 HGL Temperature | HGL Temperature | 331 | 343 | 313 | 322 | 5 | 15 | Max |  |  | 22 | 89.22 | 14.667 | 22 | 85.776 | 14.833 | 67.22 | 63.776 | -5.1233
Compare | Tree 5 HGL Height | HGL Height | 331 | 341 | 313 | 323 | 5 | 15 | Min |  |  | 2.44 | 1.23 | 12.333 | 2.44 | 0.92512 | 5.3333 | -1.21 | -1.5149 | 25.197
Compare | Tree 7 HGL Temperature | HGL Temperature | 331 | 347 | 313 | 328 | 5 | 15 | Max |  |  | 22 | 58.59 | 14.833 | 22 | 55.473 | 14.833 | 36.59 | 33.473 | -8.5187
Compare | Tree 7 HGL Height | HGL Height | 331 | 345 | 313 | 329 | 5 | 15 | Min |  |  | 2.43 | 1.02 | 13.5 | 2.43 | 0.34733 | 5.1667 | -1.41 | -2.0827 | 47.707
Experiment | NIST_Plaza | 3
Model | NIST_Plaza | 3
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Burn Room HGL Temperature | HGL Temperature | 1 | 2 | 10 | 11 | 0 | 30 | Max |  |  | 13.929 | 168.47 | 15.5 | 15 | 181.63 | 19.5 | 154.54 | 166.63 | 7.8257
Compare | Burn Room HGL Height | HGL Height | 1 | [17 empty] | No experimental measureme
Compare | Corridor HGL Temperature | HGL Temperature | 1 | 3 | 10 | 12 | 0 | 30 | Max |  |  | 15.338 | 439.36 | 13.5 | 15 | 402.76 | 19.5 | 424.02 | 387.76 | -8.5529
Compare | Corridor HGL Height | HGL Height | 1 | [17 empty] | No experimental measureme
Compare | Floor 7 HGL Temperature | HGL Temperature | 1 | 7 | 10 | 16 | 0 | 30 | Max |  |  | 14.586 | 15.168 | 25.5 | 15 | 17.28 | 19.5 | 0.582 | 2.2803 | 291.8
Compare | Floor 7 HGL Height | HGL Height | 1 | [17 empty] | No experimental measureme
Compare | Corridor Oxygen | Oxygen | 1 | 4 | 10 | 13 | 0 | 30 | Min |  |  | 20.9 | 9.87 | 14.5 | 20.544 | 12.165 | 19.5 | -11.03 | -8.3791 | -24.034
Compare | Corridor Carbon Dioxide | Carbon Dioxide | 1 | 6 | 10 | 15 | 0 | 30 | Max |  |  | 0 | 4.03 | 15 | 0 | 2.8657 | 19.5 | 4.03 | 2.8657 | -28.89
Compare | Corridor 7 Pressure | Pressure | 1 | 8 | 10 | 17 | 0 | 30 | Max |  |  | 1.9892 | 3.5834 | 6.5 | 9.5046 | 10.361 | 19.5 | 1.5942 | 0.85683 | -46.253
Experiment | fm19 | 5
Model | fm19 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 123 | 114 | 126 | 127 | 0 | 8 | Max |  |  | 21.7 | 265.83 | 7.8333 | 15 | 305.8 | 6.6667 | 244.13 | 290.8 | 19.114
Compare | Room 1 HGL Height | HGL Height | 123 | 14 | 126 | 128 | 0 | 8 | Min |  |  | 2.45 | 0.4885 | 3.1667 | 2.4498 | 1.089 | 7.8333 | -1.9615 | -1.3608 | -30.624
Compare | Room 1 Oxygen | Oxygen | 123 | 20 | 126 | 130 | 0 | 8 | Min |  |  | 20.8 | 17.7 | 5.6667 | 20.545 | 15.829 | 7.8333 | -3.1 | -4.7165 | 52.145
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 123 | 2 | 126 | 131 | 0 | 8 | Max |  |  | 0 | 2.2917 | 5.6667 | 0 | 2.457 | 7.8333 | 2.2917 | 2.457 | 7.2132
Compare | Room 1 Pressure | Pressure | 123 |  | 126 | 129 | [14 empty] | No experimental measureme
Compare | Room 2 HGL Temperature | HGL Temperature | 123 | 115 | 126 | 132 | 0 | 8 | Max |  |  | 16.7 | 72.55 | 7.8333 | 15 | 102.37 | 4.8333 | 55.85 | 87.372 | 56.44
Compare | Room 2 HGL Height | HGL Height | 123 | 11 | 126 | 133 | 0 | 8 | Min |  |  | 2.43 | 0.44 | 3.5 | 2.4298 | 0.17015 | 7.8333 | -1.99 | -2.2596 | 13.548
Compare | Room 2 HGL Temperature | HGL Temperature | 123 | 116 | 126 | 132 | 0 | 8 | Max |  |  | 16.4 | 77.4 | 7.8333 | 15 | 102.37 | 4.8333 | 61 | 87.372 | 43.233
Compare | Room 2 HGL Height | HGL Height | 123 | 12 | 126 | 133 | 0 | 8 | Min |  |  | 2.43 | 0.439 | 2 | 2.4298 | 0.17015 | 7.8333 | -1.991 | -2.2596 | 13.491
Compare | Room 2 HGL Temperature | HGL Temperature | 123 | 117 | 126 | 132 | 0 | 8 | Max |  |  | 17.2 | 93.6 | 7.8333 | 15 | 102.37 | 4.8333 | 76.4 | 87.372 | 14.361
Compare | Room 2 HGL Height | HGL Height | 123 | 13 | 126 | 133 | 0 | 8 | Min |  |  | 2.43 | 0.499 | 0 | 2.4298 | 0.17015 | 7.8333 | -1.931 | -2.2596 | 17.018
Compare | Room 2 Oxygen | Oxygen | 123 | 19 | 126 | 135 | 0 | 8 | Min |  |  | 20.6 | 16.9 | 7.8333 | 20.544 | 17.455 | 7.8333 | -3.7 | -3.0897 | -16.495
Compare | Room 2 Carbon Dioxide | Carbon Dioxide | 123 | 1 | 126 | 136 | 0 | 8 | Max |  |  | 0 | 2.0117 | 7.8333 | 0 | 1.6071 | 7.8333 | 2.0117 | 1.6071 | -20.11
Compare | Room 2 Pressure | Pressure | 123 |  | 126 | 134 | [14 empty] | No experimental measureme
Compare | Room 3 HGL Temperature | HGL Temperature | 123 | 118 | 126 | 137 | 0 | 8 | Max |  |  | 15.2 | 65.367 | 7.8333 | 15 | 57.525 | 7.8333 | 50.167 | 42.525 | -15.232
Compare | Room 3 HGL Height | HGL Height | 123 | 15 | 126 | 138 | 0 | 8 | Min |  |  | 2.45 | 0.46333 | 2.8333 | 2.4497 | 0.038549 | 7.8333 | -1.9867 | -2.4112 | 21.369
Compare | Room 3 Carbon Dioxide | Carbon Dioxide | 123 | 3 | 126 | 141 | 0 | 8 | Max |  |  | 0 | 1.7717 | 7.8333 | 0 | 1.4601 | 7.8333 | 1.7717 | 1.4601 | -17.586
Compare | Room 3 Pressure | Pressure | 123 |  | 126 | 139 | [14 empty] | No experimental measureme
Compare | Room 4 HGL Temperature | HGL Temperature | 123 | 119 | 126 | 142 | 0 | 8 | Max |  |  | 15.3 | 50.4 | 7.8333 | 15 | 58.285 | 7.8333 | 35.1 | 43.285 | 23.319
Compare | Room 4 HGL Height | HGL Height | 123 | 16 | 126 | 143 | 0 | 8 | Min |  |  | 2.43 | 0.38 | 1 | 2.4298 | 0.036217 | 7.8333 | -2.05 | -2.3935 | 16.758
Compare | Room 4 Carbon Dioxide | Carbon Dioxide | 123 | 4 | 126 | 146 | 0 | 8 | Max |  |  | 0 | 1.91 | 7.8333 | 0 | 1.4712 | 7.8333 | 1.91 | 1.4712 | -22.974
Compare | Room 4 Pressure | Pressure | 123 |  | 126 | 144 | [14 empty] | No experimental measureme
Experiment | fm21 | 5
Model | fm21 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 125 | 116 | 128 | 129 | 0 | 8 | Max |  |  | 15.5 | 360.83 | 7.8333 | 15 | 340.62 | 7.8333 | 345.33 | 325.62 | -5.7088
Compare | Room 1 HGL Height | HGL Height | 125 | 16 | 128 | 130 | 0 | 8 | Min |  |  | 2.45 | 0.731 | 4.8333 | 2.4498 | 0.18772 | 7.8333 | -1.719 | -2.262 | 31.591
Compare | Room 1 Oxygen | Oxygen | 125 | 22 | 128 | 132 | 0 | 8 | Min |  |  | 22.5 | 16.5 | 7.8333 | 20.545 | 12.04 | 7.8333 | -6 | -8.505 | 41.75
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 125 | 4 | 128 | 133 | 0 | 8 | Max |  |  | 0 | 3.2817 | 7.8333 | 0 | 4.3795 | 7.8333 | 3.2817 | 4.3795 | 33.452
Compare | Room 1 Pressure | Pressure | 125 |  | 128 | 131 | [14 empty] | No experimental measureme
Compare | Room 2 HGL Temperature | HGL Temperature | 125 | 117 | 128 | 134 | 0 | 8 | Max |  |  | 13.2 | 95.15 | 7.8333 | 15 | 117.54 | 7.8333 | 81.95 | 102.54 | 25.119
Compare | Room 2 HGL Height | HGL Height | 125 | 13 | 128 | 135 | 0 | 8 | Min |  |  | 2.43 | 0.32118 | 0.83333 | 2.4298 | 0.024588 | 7.8333 | -2.1088 | -2.4052 | 14.053
Compare | Room 2 HGL Temperature | HGL Temperature | 125 | 118 | 128 | 134 | 0 | 8 | Max |  |  | 13.1 | 104 | 7.8333 | 15 | 117.54 | 7.8333 | 90.9 | 102.54 | 12.8
Compare | Room 2 HGL Height | HGL Height | 125 | 14 | 128 | 135 | 0 | 8 | Min |  |  | 2.43 | 0.36 | 2.5 | 2.4298 | 0.024588 | 7.8333 | -2.07 | -2.4052 | 16.192
Compare | Room 2 HGL Temperature | HGL Temperature | 125 | 119 | 128 | 134 | 0 | 8 | Max |  |  | 13.4 | 127 | 7.8333 | 15 | 117.54 | 7.8333 | 113.6 | 102.54 | -9.7403
Compare | Room 2 HGL Height | HGL Height | 125 | 15 | 128 | 135 | 0 | 8 | Min |  |  | 2.43 | 0.40333 | 2.6667 | 2.4298 | 0.024588 | 7.8333 | -2.0267 | -2.4052 | 18.676
Compare | Room 2 Oxygen | Oxygen | 125 | 21 | 128 | 137 | 0 | 8 | Min |  |  | 20.8 | 16.383 | 7.8333 | 20.544 | 15.108 | 7.8333 | -4.4167 | -5.4369 | 23.1
Compare | Room 2 Carbon Dioxide | Carbon Dioxide | 125 | 1 | 128 | 138 | 0 | 8 | Max |  |  | 0 | 3.0217 | 7.8333 | 0 | 2.7999 | 7.8333 | 3.0217 | 2.7999 | -7.3386
Compare | Room 2 Carbon Dioxide | Carbon Dioxide | 125 | 2 | 128 | 138 | 0 | 8 | Max |  |  | 0 | 3.2217 | 7.8333 | 0 | 2.7999 | 7.8333 | 3.2217 | 2.7999 | -13.091
Compare | Room 2 Pressure | Pressure | 125 |  | 128 | 136 | [14 empty] | No experimental measureme
Compare | Room 3 HGL Temperature | HGL Temperature | 125 | 120 | 128 | 139 | 0 | 8 | Max |  |  | 13.2 | 86.367 | 7.8333 | 15 | 73.836 | 7.8333 | 73.167 | 58.836 | -19.586
Compare | Room 3 HGL Height | HGL Height | 125 | 17 | 128 | 140 | 0 | 8 | Min |  |  | 2.45 | 0.34 | 2.5 | 2.4497 | 0.00077061 | 7.8333 | -2.11 | -2.449 | 16.065
Compare | Room 3 Carbon Dioxide | Carbon Dioxide | 125 | 5 | 128 | 143 | 0 | 8 | Max |  |  | 0 | 2.7917 | 7.8333 | 0 | 2.3401 | 7.8333 | 2.7917 | 2.3401 | -16.176
Compare | Room 3 Pressure | Pressure | 125 |  | 128 | 141 | [14 empty] | No experimental measureme
Compare | Room 4 HGL Temperature | HGL Temperature | 125 | 120 | 128 | 144 | 0 | 8 | Max |  |  | 13.2 | 86.367 | 7.8333 | 15 | 74.901 | 7.8333 | 73.167 | 59.901 | -18.131
Compare | Room 4 HGL Height | HGL Height | 125 | 18 | 128 | 145 | 0 | 8 | Min |  |  | 2.43 | 0.32 | 1.5 | 2.4298 | 0.00058686 | 7.8333 | -2.11 | -2.4292 | 15.127
Compare | Room 4 Carbon Dioxide | Carbon Dioxide | 125 | 6 | 128 | 148 | 0 | 8 | Max |  |  | 0 | 2.8017 | 7.8333 | 0 | 2.3667 | 7.8333 | 2.8017 | 2.3667 | -15.524
Compare | Room 4 Pressure | Pressure | 125 |  | 128 | 146 | [14 empty] | No experimental measureme
Experiment | 1Room1 | 5
Model | 1Room1 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature A | HGL Temperature | 87 | 85 | 109 | 110 | 0 | 30 | Max |  |  | 22 | 791.85 | 8.3333 | 27 | 754.93 | 8.5 | 769.85 | 727.93 | -5.4457
Compare | Room 1 HGL Height A | HGL Height | 87 | 11 | 109 | 111 | 0 | 30 | Min |  |  | 2.31 | 0.23857 | 7 | 2.3098 | 0.34278 | 8 | -2.0714 | -1.967 | -5.0419
Compare | Room 1 HGL Temperature B | HGL Temperature | 87 | 86 | 109 | 110 | 0 | 30 | Max |  |  | 23.58 | 919.25 | 7.5 | 27 | 754.93 | 8.5 | 895.67 | 727.93 | -18.728
Compare | Room 1 HGL Height B | HGL Height | 87 | 12 | 109 | 111 | 0 | 30 | Min |  |  | 2.31 | 0.081511 | 7 | 2.3098 | 0.34278 | 8 | -2.2285 | -1.967 | -11.734
Compare | Room 1 Oxygen A | Oxygen | 87 | 21 | 109 | 113 | 0 | 30 | Min |  |  | 20.9 | 0 | 8 | 20.355 | 6.4442 | 8.1667 | -20.9 | -13.911 | -33.442
Compare | Room 1 Carbon Dioxide A | Carbon Dioxide | 87 | 3 | 109 | 114 | 0 | 30 | Max |  |  | 0 | 16.911 | 8 | 0 | 5.3877 | 8.1667 | 16.911 | 5.3877 | -68.141
Compare | Room 1 Oxygen B | Oxygen | 87 | 22 | 109 | 113 | 0 | 30 | Min |  |  | 20.9 | 1.3682 | 8.1667 | 20.355 | 6.4442 | 8.1667 | -19.532 | -13.911 | -28.779
Compare | Room 1 Carbon Dioxide B | Carbon Dioxide | 87 | 4 | 109 | 114 | 0 | 30 | Max |  |  | 0 | 16.153 | 8.1667 | 0 | 5.3877 | 8.1667 | 16.153 | 5.3877 | -66.646
Compare | Room 1 Pressure | Pressure | 87 |  | 109 | 112 | [14 empty] | No experimental measureme
Experiment | 1Room6 | 5
Model | 1Room6 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature A | HGL Temperature | 87 | 85 | 113 | 114 | 0 | 30 | Max |  |  | 23.43 | 587.35 | 8.5 | 27 | 636.34 | 8.6667 | 563.92 | 609.34 | 8.0549
Compare | Room 1 HGL Height A | HGL Height | 87 | 11 | 113 | 115 | 0 | 30 | Min |  |  | 2.31 | 0.076499 | 0.16667 | 2.3098 | 0.49368 | 8.5 | -2.2335 | -1.8161 | -18.689
Compare | Room 1 HGL Temperature B | HGL Temperature | 87 | 86 | 113 | 114 | 0 | 30 | Max |  |  | 25.88 | 901.75 | 8.5 | 27 | 636.34 | 8.6667 | 875.87 | 609.34 | -30.43
Compare | Room 1 HGL Height B | HGL Height | 87 | 12 | 113 | 115 | 0 | 30 | Min |  |  | 2.31 | 0.86982 | 7.6667 | 2.3098 | 0.49368 | 8.5 | -1.4402 | -1.8161 | 26.102
Compare | Room 1 Oxygen A | Oxygen | 87 | 21 | 113 | 117 | 0 | 30 | Min |  |  | 20.9 | 6.8713 | 8.1667 | 20.355 | 10.262 | 8.5 | -14.029 | -10.093 | -28.053
Compare | Room 1 Carbon Dioxide A | Carbon Dioxide | 87 | 3 | 113 | 118 | 0 | 30 | Max |  |  | 0 | 10.602 | 8.1667 | 0 | 3.9471 | 8.5 | 10.602 | 3.9471 | -62.77
Compare | Room 1 Oxygen B | Oxygen | 87 | 22 | 113 | 117 | 0 | 30 | Min |  |  | 20.9 | 10.995 | 8.1667 | 20.355 | 10.262 | 8.5 | -9.905 | -10.093 | 1.9001
Compare | Room 1 Carbon Dioxide B | Carbon Dioxide | 87 | 4 | 113 | 118 | 0 | 30 | Max |  |  | 0 | 8.1104 | 8 | 0 | 3.9471 | 8.5 | 8.1104 | 3.9471 | -51.333
Compare | Room 1 Pressure | Pressure | 87 |  | 113 | 116 | [14 empty] | No experimental measureme
Experiment | 1RWall1 | 5
Model | 1RWall1 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 83 | 82 | 110 | 111 | 0 | 30 | Max |  |  | 24.5 | 801.5 | 11.833 | 22 | 611.37 | 3.8333 | 777 | 589.37 | -24.148
Compare | Room 1 HGL Height | HGL Height | 83 | 8 | 110 | 112 | 0 | 30 | Min |  |  | 2.44 | 0.20883 | 11.833 | 2.4398 | 0.72896 | 3.6667 | -2.2312 | -1.7108 | -23.323
Compare | Room 1 Oxygen | Oxygen | 83 |  | 110 | 114
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 83 |  | 110 | 115 | [5 empty] | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 83 | 32 | 110 | 113 | 0 | 30 | Min |  |  | -0.0249 | -1.865 | 12.167 | 0 | -4.689 | 3.8333 | -1.8401 | -4.689 | 154.82
Experiment | 1RWall2 | 5
Model | 1RWall2 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 105 | 104 | 133 | 134 | 0 | 10 | Max |  |  | 23.37 | 806.75 | 8.6667 | 22 | 1215.1 | 7.3333 | 783.38 | 1193.1 | 52.305
Compare | Room 1 HGL Height | HGL Height | 105 | 8 | 133 | 135 | 0 | 10 | Min |  |  | 2.44 | 0.11027 | 8.3333 | 2.4398 | 0.6236 | 6.5 | -2.3297 | -1.8162 | -22.044
Compare | Room 1 Oxygen | Oxygen | 105 |  | 133 | 137
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 105 |  | 133 | 138 | [5 empty] | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 105 | 32 | 133 | 136 | 0 | 10 | Min |  |  | -0.17409 | -1.8901 | 8.6667 | 0 | -6.5486 | 7.6667 | -1.716 | -6.5486 | 281.62
End

## Mod vs Exp
[29 empty] | 14% | 13% | 16% | 14% | 9% | 33% | 40% | 20% | 14%
Series | Meas HGl Temp | Pred HGL Temp | Meas HGL Depth | Pred HGL Depth | Meas Jet Temp | Pred Jet Temp | Meas Plume Temp | Pred Plume Temp | Meas CO2 | Pred CO2 | Meas O2 | Pred O2 | Meas Smoke | Pred Smoke | Meas Press | Pred Press | Meas Cable Temp | Pred Cable Temp | Meas Cable Rad | Pred Cable Rad | Meas Cable Flux | Pred Cable Flux | Meas Surface Temp | Pred Surface Temp | Meas Surface Flux | Meas Surface Flux | X Error Bars | 45° line | HGT Uncert | HGT Depth Uncert | Jet Uncert | Plume Temp Uncert | Gas Concen Uncert | Smoke Uncert | Pressure Uncert | Surface Flux Uncert | Surface Temp Uncert
BE2 | 54.76 | 62.337 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 86.31 | 99.282 | [24 empty] | 1300 | 1300 | 1482 | 1469 | 1508 | 1482 | 1417 | 1729 | 1820 | 1560 | 1482
| 82.56 | 90.994 | 13.86 | 14.945
BE3 | 122.89 | 135.48 |  |  | 154.9 | 135.48 |  |  | 0.0384 | 0.044425 | 0.065 | 0.076107 | 41.5 | 319.84 | 57.6 | 42.398 | 106.4 | 102.77 | 1.1215 | 1.5319 | 1.853 | 1.6738 | 54.2 | 88.945 | 1.3849 | 1.6716 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 116.81 | 132.52 |  |  | 139.31 | 132.52 |  |  | 0.037978 | 0.042644 | 0.063915 | 0.072999 | 55.051 | 306.14 | 45.871 | 28.842 |  |  | 1.4394 | 1.5832 |  |  | 68 | 88.994 | 1.7657 | 1.6525 | 1300 |  | 1118 | 1131 | 1092 | 1118 | 1183 | 871 | 780 | 1040 | 1118
| 229.21 | 234.57 |  |  | 270.6 | 234.57 |  |  | 0.0543 | 0.058653 | 0.092 | 0.10048 | 128 | 418.82 | 290 | 266.01 | 82.6 | 67.864 | 0.86692 | 1.4342 | 1.6043 | 1.7999 | 55.4 | 88.51 | 1.2583 | 1.6706
| 217.68 | 234.06 |  |  | 246.93 | 234.06 |  |  | 0.057883 | 0.057377 | 0.096062 | 0.09824 | 99.528 | 410.64 | 189.34 | 213.95 | 64.4 | 95.956 | 1.5111 | 1.5881 |  |  | 71 | 89.118 | 1.7222 | 1.6669 | [8 empty] | 0
| 204.28 | 221.66 |  |  | 228.69 | 221.66 |  |  | 0.04737 | 0.034985 | 0.078605 | 0.059864 | 79.898 | 177.26 | 56.605 | 76.776 | 109.22 | 101.95 | 1.2041 | 1.5004 | 1.84 | 1.6273 | 38.2 | 70.94 | 0.92441 | 1.3695 | [8 empty] | -1820
| 197.83 | 221.01 |  |  | 217.55 | 221.01 |  |  | 0.046545 | 0.03473 | 0.079243 | 0.059369 | 70.747 | 176.72 | 49.326 | 45.703 | 87.264 | 102.25 | 1.3489 | 1.5507 | 2.5179 | 1.6752 | 77.4 | 69.214 | 2.3828 | 1.3363
| 290.49 | 310.87 |  |  | 330.42 | 310.87 |  |  | 0.060082 | 0.064363 | 0.10059 | 0.11017 | 223.51 | 479.93 | 231.54 | 335.6 | 90.107 | 73.313 | 0.82047 | 1.4046 | 1.5088 | 1.7076 | 80.7 | 91.93 | 1.9286 | 1.7032 | [8 empty] | 0
| 268.44 | 289.68 |  |  | 277.66 | 289.68 |  |  | 0.055209 | 0.043607 | 0.091445 | 0.074639 | 139.07 | 204.2 | 80.58 | 308.54 | 78.053 | 93.242 | 1.4704 | 1.5558 | 1.8916 | 1.6908 | 176.3 | 90.61 | 3.7541 | 1.6687 | [8 empty] | -780
| 135.33 | 143.19 |  |  | 155.85 | 143.19 |  |  | 0.021633 | 0.016648 | 0.033432 | 0.031083 | 353.09 | 1589.9 | 194.86 | 137.45 | 175.7 | 143.98 | 2.8824 | 4.1845 | 5.2605 | 4.6139 | 53.134 | 86.5 | 1.379 | 1.6397
| 207.25 | 243.33 | 2.91 | 2.8132 | 240.67 | 243.33 |  |  | 0.031099 | 0.027337 | 0.052125 | 0.044054 | 118.03 | 139.61 | -1.907 | -2.1026 | 126.3 | 145.47 | 4.1562 | 4.3326 | 9.8273 | 4.7519 | 70.29 | 86.57 | 1.8768 | 1.6196
| 203.99 | 240.56 | 2.92 | 2.8015 | 234.6 | 240.56 |  |  | 0.0313 | 0.026939 | 0.054 | 0.041929 | 117 | 138.81 | -1.96 | -2.0986 | 128.9 | 112.25 | 1.99 | 3.903 | 4.773 | 4.5654 | 54.624 | 86.122 | 1.2216 | 1.6403
| 175.49 | 198.17 | 2.95 | 2.663 | 207.74 | 198.17 |  |  | 0.017468 | 0.016122 | 0.030366 | 0.02603 | 87.335 | 90.568 | -1.8097 | -1.9599 | 106.6 | 138.22 | 5.9679 | 4.3407 |  |  | 70.155 | 86.704 | 1.7871 | 1.6349
| 208.23 | 241.62 | 2.91 | 2.8058 | 240.8 | 241.62 |  |  | 0.0322 | 0.027097 | 0.055 | 0.042021 | 91.3 | 139.24 | -2.05 | -2.1193 | 183.31 | 142 | 2.9117 | 4.1378 | 5.5839 | 4.5785 | 36.357 | 68.635 | 0.90253 | 1.3406
| 210.57 | 241.95 | 2.89 | 2.7893 | 243.66 | 241.95 |  |  | 0.031216 | 0.026688 | 0.051638 | 0.041969 | 122.72 | 139.52 | -2.3509 | -2.1996 | 149.63 | 143.53 | 3.5529 | 4.286 | 8.5136 | 4.7163 | 78.206 | 66.936 | 2.3194 | 1.3078
| 193.43 | 242.79 | 2.91 | -2.8072 | 235.01 | 242.79 |  |  | 0.030642 | 0.027184 | 0.050739 | 0.043821 | 110.18 | 139.7 | -2.0059 | -2.1449 | 131.4 | 110.95 | 1.931 | 3.856 | 4.927 | 4.5268 | 79.891 | 89.487 | 1.9418 | 1.6704
[17 empty] | 106.86 | 136.42 | 6.0252 | 4.2945 | 5.98 | 4.6571 | 191.41 | 88.149
[17 empty] | 148.76 | 155.53 | 2.9162 | 3.859 | 5.5227 | 4.1411 | 95.6 | 150.35 | 3.775 | 4.4026
[17 empty] | 113.13 | 156.78 | 3.255 | 3.9958 | 7.2296 | 4.2705 | 120.1 | 151.34 | 4.5124 | 4.3435
[17 empty] | 148.55 | 115.26 | 2.0227 | 3.6031 | 5.0236 | 4.1579 | 109.6 | 149.77 | 3.6207 | 4.397
[17 empty] | 124.93 | 148.54 | 5.9962 | 3.9824 | 6.4245 | 4.2281 | 125.4 | 150.61 | 4.62 | 4.3911
[17 empty] | 143.76 | 161.74 | 2.6898 | 3.8373 | 4.9052 | 4.0796 | 74.2 | 127.01 | 2.5919 | 3.6517
[17 empty] | 132.45 | 163.53 | 2.913 | 3.9729 | 6.7148 | 4.2052 | 156.2 | 123.53 | 8.9025 | 3.5445
[17 empty] | 150.46 | 128.55 | 1.9278 | 3.5834 | 4.3612 | 4.0372 | 147.8 | 154.15 | 5.6472 | 4.4656
[17 empty] | 148.3 | 148.87 | 5.4241 | 3.9598 | 6.2034 | 4.2012 | 308.2 | 152.01 | 14.507 | 4.3415
[17 empty] | 185.88 | 164.68 | 4.7724 | 7.6938 | 8.2647 | 8.4281 | 94.561 | 148.58 | 3.8377 | 4.363
[17 empty] | 173.4 | 168.37 | 6.5796 | 7.9837 | 11.221 | 8.6912 | 131.97 | 149.86 | 3.2551 | 4.3027
[17 empty] | 143.38 | 142.65 | 2.8973 | 7.1425 | 7.2846 | 8.0455 | 109.05 | 147.98 | 2.4635 | 4.3574
[17 empty] | 133.32 | 163.96 | 10.063 | 7.9967 | 12.176 | 8.5561 | 124.67 | 148.84 | 4.6996 | 4.3514
[17 empty] | 160.45 | 165.29 | 4.1167 | 6.5385 | 8.3662 | 7.1471 | 71.211 | 125.18 | 2.5552 | 3.6042
[17 empty] | 155.88 | 169.63 | 4.832 | 6.8064 | 11.666 | 7.3846 | 148.16 | 121.54 | 8.6335 | 3.4969
[17 empty] | 168.47 | 147.4 | 2.7579 | 6.0351 | 6.1349 | 6.7754 | 147.82 | 152.53 | 6.1416 | 4.4273
[17 empty] | 169.15 | 149.79 | 11.963 | 6.7876 | 12.228 | 7.3336 | 325.27 | 150.56 | 12.923 | 4.3021
[19 empty] | 1.299 | 2.0804 | 2.3621 | 2.5837 | 96.934 | 149.61 | 3.4102 | 3.9546
[19 empty] | 1.5215 | 2.2011 | 3.2863 | 2.6865 | 145.5 | 151.51 | 3.5068 | 3.9523
[19 empty] | 0.88131 | 1.8561 | 1.852 | 2.4061 | 105.81 | 149.18 | 3.2605 | 3.9493
[19 empty] | 2.4164 | 2.2961 | 3.0662 | 2.6604 | 120.85 | 149.69 | 3.9741 | 3.9457
[17 empty] | 225.93 | 221.37 | 4.4473 | 4.8761 | 7.103 | 4.9384 | 76.361 | 129.75 | 2.4658 | 3.3261
[17 empty] | 209.68 | 222.55 |  |  | 9.4539 | 5.1082 | 151.7 | 126.84 | 8.5108 | 3.2435
[17 empty] | 195.36 | 159.54 | 2.9529 | 4.5264 | 5.5485 | 4.9039 | 147.25 | 152.89 | 5.0838 | 4.0064
[17 empty] | 168.72 | 224.18 | 5.3629 | 5.4724 | 6.4501 | 5.5111 | 180.03 | 152.67 | 6.0192 | 3.9623
[17 empty] | 227.5 | 218.02 | 4.2937 | 4.6838 | 6.5843 | 4.7498 | 93.967 | 149.75 | 3.3458 | 3.9315
[17 empty] | 220.4 | 219.21 | 5.2581 | 4.8549 | 9.0579 | 4.9162 | 162.69 | 151.39 | 3.4816 | 3.9295
[17 empty] | 194.6 | 156.22 | 2.7315 | 4.338 | 5.08 | 4.7243 | 105.68 | 149.44 | 3.1225 | 3.9301
[17 empty] | 166.4 | 220.94 | 5.1547 | 5.2786 | 6.3723 | 5.3196 | 117.19 | 149.84 | 3.8794 | 3.9227
[17 empty] | 150.34 | 182.79 | 3.8843 | 3.605 | 6.8597 | 3.647 | 71.047 | 129.65 | 2.2749 | 3.3052
[17 empty] | 132.39 | 184.24 | 4.7816 | 3.7432 | 8.5151 | 3.7799 | 157.89 | 126.74 | 7.8927 | 3.2236
[17 empty] | 174.88 | 127.91 | 2.6462 | 3.3154 | 6.4487 | 3.6386 | 137.86 | 152.96 | 4.7915 | 3.9828
[17 empty] | 161 | 190.26 | 5.4464 | 4.22 | 6.6852 | 4.2338 | 221.12 | 152.55
[17 empty] | 199 | 206.71 | 2.8398 | 4.1451 | 3.8193 | 4.2643 | 110.36 | 194.7
[17 empty] | 178.3 | 207.77 |  |  | 6.0732 | 4.4282 | 199.43 | 197.84
[17 empty] | 171.2 | 144.81 | 2.1188 | 3.8779 | 3.4636 | 4.3476 | 126.58 | 193.88
[17 empty] | 269.9 | 261.9 | 10.501 | 7.2915 | 10.901 | 7.2528 | 144.91 | 195.3
[17 empty] | 415.57 | 207.01 | 46.487 | 3.8823 | 57.721 | 4.0022 | 89.208 | 166
[17 empty] | 243.37 | 208.74 |  |  | 20.872 | 4.161 | 148.76 | 160.85
[17 empty] | 669.41 | 154.81 | 18.287 | 3.6167 | 23.944 | 4.0277 | 319.28 | 196.23
[17 empty] | 161.06 | 263.34 | 3.7305 | 7.0608 | 5.124 | 7.0182 | 498.07 | 196.62
[17 empty] | 235.69 | 227.05 | 5.2342 | 5.1001 | 7.6097 | 5.1401 | 106.85 | 175.1
[17 empty] | 217.21 | 221.5 |  |  | 7.8345 | 5.0065 | 217.13 | 179.81
[17 empty] | 231.5 | 188.15 | 5.1808 | 5.708 | 8.7351 | 5.9157 | 123.22 | 174.44
[19 empty] | 2.8461 | 4.3872 | 4.4495 | 4.4939 | 141.16 | 175.28
[21 empty] | 27.18 | 36.532 | 80.012 | 147.78
[21 empty] | 46.555 | 37.269 | 145.87 | 143.28
[21 empty] | 32.413 | 35.759 | 283.68 | 177.65
[21 empty] | 2.91 | 1.62 | 441.38 | 179.19
[23 empty] | 39.006 | 52.895 | 1.4618 | 2.1086
[21 empty] | 96.68 | 2.1556 | 82.059 | 65.248 | 0.92901 | 2.2775
[23 empty] | 56.478 | 51.569 | 1.5595 | 2.1062
[21 empty] | 5.75 | 2.1542 | 61.024 | 54.038 | 1.899 | 2.0973
[23 empty] | 24.436 | 34.11 | 0.85627 | 1.3776
[23 empty] | 51.919 | 32.526 | 1.4991 | 1.3235
[23 empty] | 68.643 | 57.735
[23 empty] | 229.79 | 64.352
[23 empty] | 114.33 | 187.23 | 3.4986 | 4.4532
[23 empty] | 172.39 | 202.94 | 4.3205 | 5.0084
[23 empty] | 87.285 | 152.2 | 2.5288 | 3.5956
[23 empty] | 145.78 | 190.95 | 4.446 | 4.5805
[23 empty] | 53.598 | 142.73 | 1.9712 | 3.1937
[23 empty] | 118.69 | 138.6 | 4.0716 | 3.0854
[23 empty] | 155.21 | 194.16 | 4.6169 | 4.6603
[23 empty] | 287.38 | 197.41 | 9.8764 | 4.7752
[23 empty] | 112.9 | 183.61 | 3.4162 | 4.2672
[23 empty] | 177.9 | 199.78 | 4.2045 | 4.8213
[23 empty] | 88.1 | 147.9 | 2.418 | 3.4245
[23 empty] | 134.9 | 187.59
[23 empty] | 53.1 | 138.73 | 1.9116 | 3.0359
[23 empty] | 121.8 | 134.56 | 3.8865 | 2.9301
[23 empty] | 203.6 | 190.55 | 5.4505 | 4.4642
[23 empty] | 289.9 | 194.23 | 9.4103 | 4.5899
[23 empty] | 93.718 | 145.67 | 2.6847 | 3.0679
[23 empty] | 154.56 | 168.06 | 3.8129 | 3.7265
[23 empty] | 71.394 | 115.78 | 1.9983 | 2.5357
[23 empty] | 117.59 | 147.88 | 3.2917 | 3.1221
[23 empty] | 41.655 | 106.86 | 1.3997 | 2.1874
[23 empty] | 170.76 | 104.33 | 10.055 | 2.1351
[23 empty] | 125.27 | 151.15 | 3.3715 | 3.1846
[23 empty] | 263.41 | 158.77 | 6.7402 | 3.414
[23 empty] | 114.4 | 184.23 | 3.4995 | 4.3033
[23 empty] | 254.7 | 221.9 | 8.1035 | 5.6733
[23 empty] | 86.8 | 148.96 | 2.3515 | 3.5088
[23 empty] | 147.6 | 188.92 | 4.4708 | 4.4613
[23 empty] | 52.2 | 140.67 | 1.8926 | 3.0998
[23 empty] | 103.8 | 136.55 | 2.969 | 2.9942
[23 empty] | 157.7 | 192.22 | 4.6945 | 4.5419
[23 empty] | 351.8 | 200.39 | 8.9935 | 4.8348
[23 empty] | 219.66 | 183.29 | 3.6352 | 4.0693
[23 empty] | 205.45 | 187.59 | 7.4632 | 4.2069
[23 empty] | 96.276 | 144.87 | 2.6102 | 3.2579
[23 empty] | 151.44 | 187.21 | 4.6546 | 4.1944
[23 empty] | 52.299 | 136.56 | 1.9485 | 2.8519
[23 empty] | 131.58 | 132.36 | 5.2316 | 2.7506
[23 empty] | 156.87 | 190.75
[23 empty] | 287.15 | 186.12
[23 empty] | 118.16 | 184.63 | 3.4041 | 4.2703
[23 empty] | 312.36 | 248.3
[23 empty] | 94.013 | 154.22 | 2.5826 | 3.5242
[23 empty] | 152.9 | 190.34 | 4.6654 | 4.4936
[23 empty] | 49.57 | 141.32 | 1.7895 | 3.1074
[23 empty] | 106.6 | 137.25 | 3.0569 | 3.0031
[23 empty] | 144.9 | 192.93 | 4.4785 | 4.5494
[23 empty] | 250.11 | 193.63
[23 empty] | 595.74 | 546.19
[23 empty] | 721.67 | 237.94
[23 empty] | 55.9 | 36.563
[23 empty] | 4.41 | 23.912
[23 empty] | 87.35 | 36.217
[23 empty] | 68.02 | 34.71
[23 empty] | 86.16 | 36.927
[23 empty] | 71.81 | 36.686
iBMB | 700.14 | 602.31 | 4.2 | 5.0756 | [12 empty] | 356 | 359.67 |  |  | 27.18 | 36.532 | 595.74 | 546.19
[17 empty] | 308.15 | 412.79 |  |  | 46.555 | 37.269 | 721.67 | 237.94
[17 empty] | 489.15 | 514 |  |  | 32.413 | 35.759
BE5 | 150.81 | 171.59 | 4.3187 | 3.4412 |  |  |  |  | 0.012938 | 0.011777 | 0.023289 | 0.019683 |  |  |  |  | 87.22 | 66.342 |  |  | 2.91 | 1.62 | 55.9 | 36.563
[17 empty] | 111.68 | 84.905 |  |  |  |  | 4.41 | 23.912
[17 empty] | 109.75 | 87.23 |  |  | 96.68 | 2.1556 | 87.35 | 36.217
[17 empty] | 146.25 | 114.15 |  |  |  |  | 68.02 | 34.71
[17 empty] | 106.69 | 87.154 |  |  | 5.75 | 2.1542 | 86.16 | 36.927
[17 empty] | 140.25 | 113.13 |  |  |  |  | 71.81 | 36.686
FM SNL | 59.187 | 68.938 |  |  | 82.18 | 133.49
| 44.465 | 49.21 |  |  | 65.78 | 102.45
| 65.96 | 87.966 |  |  | 70.419 | 101.07
[5 empty] | 52.56 | 74.983
[5 empty] | 74.504 | 159
[5 empty] | 77.196 | 124.3
FM NBS | 244.13 | 290.8 | 1.9615 | 1.3608 |  |  |  |  | 0.022917 | 0.02457 | 0.031 | 0.047165
| 55.85 | 87.372 | 1.99 | 2.2596 |  |  |  |  | 0.020117 | 0.016071 | 0.037 | 0.030897
| 61 | 87.372 | 1.991 | 2.2596 |  |  |  |  | 0.017717 | 0.014601
| 76.4 | 87.372 | 1.931 | 2.2596 |  |  |  |  | 0.0191 | 0.014712
| 50.167 | 42.525 | 1.9867 | 2.4112 |  |  |  |  | 0.032817 | 0.043795 | 0.06 | 0.08505
| 43.285 | 23.319 | 2.05 | 2.3935 |  |  |  |  | 0.030217 | 0.027999 | 0.044167 | 0.054369
| 345.33 | 325.62 | 1.719 | 2.262 |  |  |  |  | 0.032217 | 0.027999
| 81.95 | 102.54 | 2.1088 | 2.4052 |  |  |  |  | 0.027917 | 0.023401
| 90.9 | 102.54 | 2.07 | 2.4052
| 113.6 | 102.54 | 2.0267 | 2.4052
| 73.167 | 58.836 | 2.11 | 2.449
| 73.167 | 59.901 | 2.11 | 2.4292
NBS | 259.39 | 237.43 | 1.27 | 1.3187 |  |  |  |  | 0.209 | 0.13911 | 0.16911 | 0.053877 |  |  | -1.8401 | -4.689
| 86.16 | 88.057 | 1.17 | 1.1858 |  |  |  |  | 0.19532 | 0.13911 | 0.16153 | 0.053877 |  |  | -1.716 | -6.5486
| 77.28 | 88.057 | 1.29 | 1.1858 |  |  |  |  | 0.14029 | 0.10093 | 0.10602 | 0.039471
| 74.3 | 88.057 | 1.18 | 1.1858 |  |  |  |  | 0.09905 | 0.10093 | 0.081104 | 0.039471
| 312 | 335.65
| 106.2 | 74.789
| 99.33 | 74.789
| 285.67 | 240.33 | 1.34 | 1.3204
| 67.08 | 63.776 | 1.17 | 1.5149
| 67.22 | 63.776 | 1.21 | 1.5149
| 36.59 | 33.473 | 1.41 | 2.0827
| 769.85 | 727.93 | 2.0714 | 1.967
| 895.67 | 727.93 | 2.2285 | 1.967
| 563.92 | 609.34 | 2.2335 | 1.8161
| 875.87 | 609.34 | 1.4402 | 1.8161
| 777 | 589.37 | 2.2312 | 1.7108
| 783.38 | 1193.1 | 2.3297 | 1.8162
NIST Plaza | 154.54 | 166.63 | [6 empty] | 0.0403 | 0.028657 | 0.1103 | 0.083791
| 424.02 | 387.76
| 0.582 | 2.2803

## HGT & HGL
[9 empty] | Absolute Values |  |  | Averages by Series
|  |  | Hot Gas Layer Temperature Rise |  |  | Hot Gas Layer Depth |  |  | HGL Temperature | HGL Depth |  | HGL Temperature | HGL Depth
Series | Test | Measurement Position | Exp | CFAST | Relative Difference | Exp | CFAST | Relative Difference | Relative Difference | Relative Difference | Series | Relative Difference | Relative Difference
|  |  | (°C) | (°C) | (%) | (m) | (m) | (%) | (%) | (%) |  | (%) | (%)
VTT | Case 1 |  | 54.76 | 62.337 | 13.836 |  |  |  | 13.836 |  | BE2 | 13.0273 | 7.8253
| Case 2 |  | 86.31 | 99.282 | 15.03 |  |  |  | 15.03
| Case 3 |  | 82.56 | 90.994 | 10.216 | 13.86 | 14.945 | 7.8253 | 10.216 | 7.8253
NIST / NRC | Test 1 |  | 122.89 | 135.48 | 10.246 |  |  |  | 10.246 |  | BE3 | 11.9494 | 4.6188
| Test 7 |  | 116.81 | 132.52 | 13.452 |  |  |  | 13.452
| Test 2 |  | 229.21 | 234.57 | 2.3367 |  |  |  | 2.3367
| Test 8 |  | 217.68 | 234.06 | 7.5234 |  |  |  | 7.5234
| Test 4 |  | 204.28 | 221.66 | 8.5104 |  |  |  | 8.5104
| Test 10 |  | 197.83 | 221.01 | 11.718 |  |  |  | 11.718
| Test 13 |  | 290.49 | 310.87 | 7.0164 |  |  |  | 7.0164
| Test 16 |  | 268.44 | 289.68 | 7.9139 |  |  |  | 7.9139
| Test 17 |  | 135.33 | 143.19 | 5.8102 |  |  |  | 5.8102
| Test 3 |  | 207.25 | 243.33 | 17.409 | 2.91 | 2.8132 | -3.3265 | 17.409 | 3.3265
| Test 9 |  | 203.99 | 240.56 | 17.929 | 2.92 | 2.8015 | -4.0589 | 17.929 | 4.0589
| Test 5 |  | 175.49 | 198.17 | 12.922 | 2.95 | 2.663 | -9.7305 | 12.922 | 9.7305
| Test 14 |  | 208.23 | 241.62 | 16.037 | 2.91 | 2.8058 | -3.5801 | 16.037 | 3.5801
| Test 15 |  | 210.57 | 241.95 | 14.9 | 2.89 | 2.7893 | -3.4837 | 14.9 | 3.4837
| Test 18 |  | 193.43 | 242.79 | 25.517 | 2.91 | -2.8072 | 3.533 | 25.517 | 3.533
iBMB | Test 1 |  | 700.14 | 602.31 | -13.974 | 4.2 | 5.0756 | 20.849 | 13.974 | 20.849 | BE4 | 13.974 | 20.849
iBMB | Test 4 |  | 150.81 | 171.59 | 13.78 | 4.3187 | 3.4412 | -20.318 | 13.78 | 20.318 | BE5 | 13.78 | 20.318
FM SNL | Test 4 |  | 59.187 | 68.938 | 16.476 |  |  |  | 16.476 |  | FM SNL | 20.1703
| Test 5 |  | 44.465 | 49.21 | 10.672 |  |  |  | 10.672
| Test 21 |  | 65.96 | 87.966 | 33.363 |  |  |  | 33.363
FM NBS | FM 19 | Burn Room | 244.13 | 290.8 | 19.114 | 1.9615 | 1.3608 | -30.624 | 19.114 | 30.624 | FM NBS | 21.8987 | 18.7093
|  | Corridor | 55.85 | 87.372 | 56.44 | 1.99 | 2.2596 | 13.548 | 56.44 | 13.548
|  | Corridor | 61 | 87.372 | 43.233 | 1.991 | 2.2596 | 13.491 | 43.233 | 13.491
|  | Corridor | 76.4 | 87.372 | 14.361 | 1.931 | 2.2596 | 17.018 | 14.361 | 17.018
|  | Target Room 1 | 50.167 | 42.525 | -15.232 | 1.9867 | 2.4112 | 21.369 | 15.232 | 21.369
|  | Target Room 2 | 43.285 | 23.319 | 23.319 | 2.05 | 2.3935 | 16.758 | 23.319 | 16.758
| FM 21 | Burn Room | 345.33 | 325.62 | -5.7088 | 1.719 | 2.262 | 31.591 | 5.7088 | 31.591
|  | Corridor | 81.95 | 102.54 | 25.119 | 2.1088 | 2.4052 | 14.053 | 25.119 | 14.053
|  | Corridor | 90.9 | 102.54 | 12.8 | 2.07 | 2.4052 | 16.192 | 12.8 | 16.192
|  | Corridor | 113.6 | 102.54 | -9.7403 | 2.0267 | 2.4052 | 18.676 | 9.7403 | 18.676
|  | Target Room 1 | 73.167 | 58.836 | -19.586 | 2.11 | 2.449 | 16.065 | 19.586 | 16.065
|  | Target Room 2 | 73.167 | 59.901 | -18.131 | 2.11 | 2.4292 | 15.127 | 18.131 | 15.127
NBS | MV100A | Burn Room | 259.39 | 237.43 | -8.4672 | 1.27 | 1.3187 | 3.8318 | 8.4672 | 3.8318 | NBS | 12.6757 | 14.6991
|  | Corridor 18 | 86.16 | 88.057 | 2.2017 | 1.17 | 1.1858 | 1.347 | 2.2017 | 1.347
|  | Corridor 38 | 77.28 | 88.057 | 13.945 | 1.29 | 1.1858 | -8.0806 | 13.945 | 8.0806
|  | Corridor Exit | 74.3 | 88.057 | 18.515 | 1.18 | 1.1858 | 0.48813 | 18.515 | 0.48813
| MV100O | Burn Room | 312 | 335.65 | 7.5804 |  |  |  | 7.5804
|  | Corridor 18 | 106.2 | 74.789 | -29.577 |  |  |  | 29.577
|  | Corridor 38 | 99.33 | 74.789 | -24.706 |  |  |  | 24.706
Corridor Exit
| MV100Z | Burn Room | 285.67 | 240.33 | -15.873 | 1.34 | 1.3204 | -1.464 | 15.873 | 1.464
|  | Corridor 18 | 67.08 | 63.776 | -4.9253 | 1.17 | 1.5149 | 29.477 | 4.9253 | 29.477
|  | Corridor 38 | 67.22 | 63.776 | -5.1233 | 1.21 | 1.5149 | 25.197 | 5.1233 | 25.197
|  | Target Room | 36.59 | 33.473 | -8.5187 | 1.41 | 2.0827 | -47.707 | 8.5187 | 47.707
| Test F1 | Burn Room | 769.85 | 727.93 | -5.4457 | 2.0714 | 1.967 | -5.0419 | 5.4457 | 5.0419 |  | 15.6646 | 15.3917
|  |  | 895.67 | 727.93 | -18.728 | 2.2285 | 1.967 | -11.734 | 18.728 | 11.734
| Test F6 | Burn Room | 563.92 | 609.34 | 8.0549 | 2.2335 | 1.8161 | -18.689 | 8.0549 | 18.689
|  |  | 875.87 | 609.34 | -30.43 | 1.4402 | 1.8161 | 26.102 | 30.43 | 26.102
| Test W1 | Burn Room | 777 | 589.37 | -24.148 | 2.2312 | 1.7108 | -23.323 | 24.148 | 23.323 |  | 38.2265 | 22.6835
| Test W2 | Burn Room | 783.38 | 1193.1 | 52.305 | 2.3297 | 1.8162 | -22.044 | 52.305 | 22.044
NIST Plaza | Test 7 | Burn Room | 154.54 | 166.63 | 7.8257 |  |  |  | 7.8257 |  | NIST Plaza | 8.1893
|  | Corridor | 424.02 | 387.76 | -8.5529 |  |  |  | 8.5529
|  | Floor 7 | 0.582 | 2.2803 | 291.8 |  |  |  | 291.8
Average ----> |  |  |  |  | 6.1215 |  |  | 2.8381 | 16.0055 | 15.0212
Standard Deviation ----> |  |  |  |  | 18.6323 |  |  | 18.3894 | 11.1505 | 10.6859
Median ----> |  |  |  |  | 8.5104 |  |  | 3.533 | 13.945 | 15.127
Percentile ranking at uncertainty limit ----> | [8 empty] | 0.519 | 0.403
90th percentile value (90 % of predictions are within xxx %) ----> | [8 empty] | 30.0888 | 28.127

## Plume Temp
[6 empty] | Absolute Values |  | Averages by Series
|  |  | Plume Temperature Rise |  |  | Plume Temperature |  | HGL Temperature
Series | Test | Measurement Position | Exp | CFAST | Relative Difference | Relative Difference | Series | Relative Difference
|  |  | (°C) | (°C) | (%) | (%) |  | (%)
VTT | Case 1 | [5 empty] | VTT | #DIV/0!
Case 2
Case 3
FM SNL | Test 4 |  | 114.2 | 127.69 | 11.816 | 11.816 | FM SNL | 11.816
Test 5
Test 21
Average ----> |  |  |  |  | 11.816 | 11.816
Standard Deviation ----> |  |  |  |  | #DIV/0! | #DIV/0!
Median ----> |  |  |  |  | 11.816 | 11.816
Percentile ranking at uncertainty limit ----> | [5 empty] | #N/A
90th percentile value (90 % of predictions are within xxx %) ----> | [5 empty] | 11.816

## Ceiling Jet
Comparison of ceiling jet temperature with upper gas layer temperature
|  |  | Ceiling Jet Temperature Rise |  |  | Absolute Values
Series | Test | Measurement Position | Exp | CFAST | Relative Difference | Relative Difference | Series | Test | Measurement Position | Ceiling Jet | HGT | Difference
|  |  | (°C) | (°C) | (%) | (%) |  |  |  | (°C) | (°C) | (°C)
NIST / NRC | Test 1 |  | 154.9 | 135.48 | -12.536 | 12.536 | BE3 | Test 1 |  | 154.9 | 122.89 | 32.01
| Test 7 |  | 139.31 | 132.52 | -4.8704 | 4.8704 |  | Test 7 |  | 139.31 | 116.81 | 22.5
| Test 2 |  | 270.6 | 234.57 | -13.316 | 13.316 |  | Test 2 |  | 270.6 | 229.21 | 41.39
| Test 8 |  | 246.93 | 234.06 | -5.2135 | 5.2135 |  | Test 8 |  | 246.93 | 217.68 | 29.25
| Test 4 |  | 228.69 | 221.66 | -3.0705 | 3.0705 |  | Test 4 |  | 228.69 | 204.28 | 24.41
| Test 10 |  | 217.55 | 221.01 | 1.5922 | 1.5922 |  | Test 10 |  | 217.55 | 197.83 | 19.72
| Test 13 |  | 330.42 | 310.87 | -5.9165 | 5.9165 |  | Test 13 |  | 330.42 | 290.49 | 39.93
| Test 16 |  | 277.66 | 289.68 | 4.3302 | 4.3302 |  | Test 16 |  | 277.66 | 268.44 | 9.22
| Test 17 |  | 155.85 | 143.19 | -8.122 | 8.122 |  | Test 17 |  | 155.85 | 135.33 | 20.52
| Test 3 |  | 240.67 | 243.33 | 1.1062 | 1.1062 |  | Test 3 |  | 240.67 | 207.25 | 33.42
| Test 9 |  | 234.6 | 240.56 | 2.5422 | 2.5422 |  | Test 9 |  | 234.6 | 203.99 | 30.61
| Test 5 |  | 207.74 | 198.17 | -4.6082 | 4.6082 |  | Test 5 |  | 207.74 | 175.49 | 32.25
| Test 14 |  | 240.8 | 241.62 | 0.34177 | 0.34177 |  | Test 14 |  | 240.8 | 208.23 | 32.57
| Test 15 |  | 243.66 | 241.95 | -0.70545 | 0.70545 |  | Test 15 |  | 243.66 | 210.57 | 33.09
| Test 18 |  | 235.01 | 242.79 | 3.3097 | 3.3097 |  | Test 18 |  | 235.01 | 193.43 | 41.58
FM SNL | Test 4 | Sec 1 | 82.18 | 133.49 | 62.434 | 62.434 | FM SNL | Test 4 | Sec 1 | 82.18 | 59.187 | 22.993
|  | Sec 3 | 65.78 | 102.45 | 55.745 | 55.745 |  |  | Sec 3 | 65.78 | 59.187 | 6.593
| Test 5 | Sec 1 | 70.419 | 101.07 | 43.523 | 43.523 |  | Test 5 | Sec 1 | 70.419 | 44.465 | 25.954
|  | Sec 3 | 52.56 | 74.983 | 42.662 | 42.662 |  |  | Sec 3 | 52.56 | 44.465 | 8.095
| Test 21 | Sec 1 | 74.504 | 159 | 113.41 | 113.41 |  | Test 21 | Sec 1 | 74.504 | 65.96 | 8.544
|  | Sec 3 | 77.196 | 124.3 | 61.021 | 61.021 |  |  | Sec 3 | 77.196 | 65.96 | 11.236
Average ----> |  |  |  |  | 15.8885 | 21.4465
Standard Deviation ----> |  |  |  |  | 33.5868 | 30.1693
Median ----> | [5 empty] | 5.2135
Percentile ranking at uncertainty limit ----> | [5 empty] | 0.704
90th percentile value (90 % of predictions are within xxx %) ----> | [5 empty] | 61.021
90th percentile not counting FM tests ----> | [5 empty] | 10.7704

## Gas Concentration
[9 empty] | Absolute Value |  | Average by Test Series
|  |  | HGL Oxygen Concentration Decrease |  |  | HGL Carbon Dioxide Concentration |  |  | O2 | CO2
Series | Test | Measurement Position | Exp | CFAST | Relative Difference | Exp | CFAST | Relative Difference | Relative Difference | Relative Difference
|  |  | (molar fraction) | (molar fraction) | (%) | (molar fraction) | (molar fraction) | (%) | (%) | (%)
NIST / NRC | Test 1 |  | 0.065 | 0.076107 | 17.088 | 0.0384 | 0.044425 | 15.691 | 17.088 | 15.691 | 15.6478 | 14.3301
| Test 7 |  | 0.063915 | 0.072999 | 14.213 | 0.037978 | 0.042644 | 12.287 | 14.213 | 12.287
| Test 2 |  | 0.092 | 0.10048 | 9.2196 | 0.0543 | 0.058653 | 8.0162 | 9.2196 | 8.0162
| Test 8 |  | 0.096062 | 0.09824 | 2.2675 | 0.057883 | 0.057377 | -0.87288 | 2.2675 | 0.87288
| Test 4 |  | 0.078605 | 0.059864 | -23.842 | 0.04737 | 0.034985 | -26.146 | 23.842 | 26.146
| Test 10 |  | 0.079243 | 0.059369 | -25.08 | 0.046545 | 0.03473 | -25.385 | 25.08 | 25.385
| Test 13 |  | 0.10059 | 0.11017 | 9.5264 | 0.060082 | 0.064363 | 7.1254 | 9.5264 | 7.1254
| Test 16 |  | 0.091445 | 0.074639 | -18.379 | 0.055209 | 0.043607 | -21.015 | 18.379 | 21.015
| Test 17 |  | 0.033432 | 0.031083 | -7.0259 | 0.021633 | 0.016648 | -23.044 | 7.0259 | 23.044
| Test 3 |  | 0.052125 | 0.044054 | -15.484 | 0.031099 | 0.027337 | -12.098 | 15.484 | 12.098
| Test 9 |  | 0.054 | 0.041929 | -22.354 | 0.0313 | 0.026939 | -13.932 | 22.354 | 13.932
| Test 5 |  | 0.030366 | 0.02603 | -14.28 | 0.017468 | 0.016122 | -7.7014 | 14.28 | 7.7014
| Test 14 |  | 0.055 | 0.042021 | -23.598 | 0.0322 | 0.027097 | -15.848 | 23.598 | 15.848
| Test 15 |  | 0.051638 | 0.041969 | -18.725 | 0.031216 | 0.026688 | -14.504 | 18.725 | 14.504
| Test 18 |  | 0.050739 | 0.043821 | -13.634 | 0.030642 | 0.027184 | -11.285 | 13.634 | 11.285
iBMB | Test 4 |  | 0.023289 | 0.019683 | -15.485 | 0.012938 | 0.011777 | -8.9753 | 15.485 | 8.9753 | 15.485 | 8.9753
FM NBS | FM19 | Burn Room | 0.031 | 0.047165 | 52.145 | 0.022917 | 0.02457 | 7.2132 | 52.145 | 7.2132 | 33.3725 | 17.0516
|  | Corridor | 0.037 | 0.030897 | -16.495 | 0.020117 | 0.016071 | -20.11 | 16.495 | 20.11
|  | Target Room 1 |  |  |  | 0.017717 | 0.014601 | -17.586 |  | 17.586
|  | Target Room 2 |  |  |  | 0.0191 | 0.014712 | -22.974 |  | 22.974
| FM21 | Burn Room | 0.06 | 0.08505 | 41.75 | 0.032817 | 0.043795 | 33.452 | 41.75 | 33.452
|  | Corridor | 0.044167 | 0.054369 | 23.1 | 0.030217 | 0.027999 | -7.3386 | 23.1 | 7.3386
|  | Corridor |  |  |  | 0.032217 | 0.027999 | -13.091 |  | 13.091
|  | Target Room 1 |  |  |  | 0.027917 | 0.023401 | -16.176 |  | 16.176
|  | Target Room 2 |  |  |  | 0.028017 | 0.023667 | -15.524 |  | 15.524
NBS | Test F1 | Burn Room | 0.209 | 0.13911 | -33.442 | 0.16911 | 0.053877 | -68.141 | 33.442 | 68.141 | 23.0435 | 62.2225
|  |  | 0.19532 | 0.13911 | -28.779 | 0.16153 | 0.053877 | -66.646 | 28.779 | 66.646
| Test F6 | Burn Room | 0.14029 | 0.10093 | -28.053 | 0.10602 | 0.039471 | -62.77 | 28.053 | 62.77
|  |  | 0.09905 | 0.10093 | 1.9001 | 0.081104 | 0.039471 | -51.333 | 1.9001 | 51.333
NIST Plaza |  |  | 0.1103 | 0.083791 | -24.034 | 0.0403 | 0.028657 | -28.89 | 24.034 | 28.89 | 24.034 | 28.89
Average ----> |  |  |  |  | -5.5603 |  |  | -15.8176 | 19.8277 | 21.5959
Standard Deviation ----> | [8 empty] | 11.4067 | 17.8206
Median ----> | [8 empty] | 18.379 | 15.7695
Percentile ranking at uncertainty limit ----> | [8 empty] | 0.12 | 0.207
90th percentile value (90 % of predictions are within xxx %) ----> | [8 empty] | 31.5768 | 52.4767

## Smoke Concentration
Smoke Concentration
Series | Test | Exp | CFAST | Relative Difference
|  | (mg/m3) | (mg/m3) | (%)
NIST / NRC | Test 1 | 41.5 | 319.84 | 670.69
| Test 7 | 55.051 | 306.14 | 456.09
| Test 2 | 128 | 418.82 | 227.2
| Test 8 | 99.528 | 410.64 | 312.58
| Test 4 | 79.898 | 177.26 | 121.86
| Test 10 | 70.747 | 176.72 | 149.79
| Test 13 | 223.51 | 479.93 | 114.72
| Test 16 | 139.07 | 204.2 | 46.832
| Test 17 | 353.09 | 1589.9 | 350.28
| Test 3 | 118.03 | 139.61 | 18.28
| Test 9 | 117 | 138.81 | 18.643
| Test 5 | 87.335 | 90.568 | 3.7023
| Test 14 | 91.3 | 139.24 | 52.512
| Test 15 | 122.72 | 139.52 | 13.69
| Test 18 | 110.18 | 139.7 | 26.79
Average ----> |  |  |  | 172.244
| Closed door tests ----> |  |  | 272.2269
| Open door tests ----> |  |  | 22.2695
Median ----> |  |  |  | 114.72
227.2
18.4615
Percentile ranking closed door tests ---> |  |  |  | 0
Percentile ranking open door tests ---> |  |  |  | 0.824
90th percentile value closed door tests |  |  |  | 499.01
90th percentile value open door tests |  |  |  | 39.651

## Pressure
Comparment Pressure Rise
Series | Test | Exp | CFAST | Relative Difference
|  | (Pa) | (Pa) | (%)
NIST / NRC | Test 1 | 57.6 | 42.398 | -26.392 | 26.392
| Test 7 | 45.871 | 28.842 | -37.123 | 37.123
| Test 2 | 290 | 266.01 | -8.2721 | 8.2721
| Test 8 | 189.34 | 213.95 | 13 | 13
| Test 4 | 56.605 | 76.776 | 35.636 | 35.636
| Test 10 | 49.326 | 45.703 | -7.3442 | 7.3442
| Test 13 | 231.54 | 335.6 | 44.943 | 44.943
| Test 16 | 80.58 | 308.54 | 282.91 | 282.91
| Test 17 | 194.86 | 137.45 | -29.465 | 29.465
| Test 3 | -1.907 | -2.1026 | 10.259 | 10.259
| Test 9 | -1.96 | -2.0986 | 7.0704 | 7.0704
| Test 5 | -1.8097 | -1.9599 | 8.2963 | 8.2963
| Test 14 | -2.05 | -2.1193 | 3.3785 | 3.3785
| Test 15 | -2.3509 | -2.1996 | -6.4345 | 6.4345
| Test 18 | -2.0059 | -2.1449 | 6.93 | 6.93
NBS | Test W1 | -1.8401 | -4.689 | 154.82 | 154.82
| Test W2 | -1.716 | -6.5486 | 281.62 | 281.62
Average ----> |  |  |  | 43.1666 | 56.6996
Standard Deviation ----> |  |  |  | 99.5267 | 92.0304
Median ----> |  |  |  |  | 13
Percentile ranking at uncertainty limit ----> |  |  |  |  | 0.772
90th percentile value ----> |  |  |  |  | 205.54
90th percentile value not counting NBS ----> |  |  |  |  | 41.815

## Target Flux and Temperature
|  |  | Radiant Heat Flux to Targets |  |  | Total Heat Flux to Targets |  |  | Target Temperature Rise |  |  | Rad Flux | Total Flux | Temp
| Test | Position | Exp | CFAST | Diff | Exp | CFAST | Diff | Exp | CFAST | Diff | Diff
|  |  | (kW/m2) | (kW/m2) | (%) | (kW/m2) | (kW/m2) | (%) | (°C) | (°C) | (%) | (%)
NIST / NRC | Test 1 | B | 1.1215 | 1.5319 | 36.594 | 1.853 | 1.6738 | -9.6679 | 106.4 | 102.77 | -3.4098 | 36.594 | 9.6679 | 3.4098
|  | D | 1.4394 | 1.5832 | 9.9949 | [6 empty] | 9.9949
|  | F | 0.86692 | 1.4342 | 65.435 | 1.6043 | 1.7999 | 12.194 | 82.6 | 67.864 | -17.84 | 65.435 | 12.194 | 17.84
|  | G33 | 1.5111 | 1.5881 | 5.0973 |  |  |  | 64.4 | 95.956 | 49 | 5.0973 |  | 49
| Test 7 | B | 1.2041 | 1.5004 | 24.605 | 1.84 | 1.6273 | -11.558 | 109.22 | 101.95 | -6.6576 | 24.605 | 11.558 | 6.6576
|  | D | 1.3489 | 1.5507 | 14.955 | 2.5179 | 1.6752 | -33.468 | 87.264 | 102.25 | 17.17 | 14.955 | 33.468 | 17.17
|  | F | 0.82047 | 1.4046 | 71.195 | 1.5088 | 1.7076 | 13.176 | 90.107 | 73.313 | -18.638 | 71.195 | 13.176 | 18.638
|  | G33 | 1.4704 | 1.5558 | 5.8111 | 1.8916 | 1.6908 | -10.617 | 78.053 | 93.242 | 19.46 | 5.8111 | 10.617 | 19.46
| Test 2 | B | 2.8824 | 4.1845 | 45.174 | 5.2605 | 4.6139 | -12.291 | 175.7 | 143.98 | -18.056 | 45.174 | 12.291 | 18.056
|  | D | 4.1562 | 4.3326 | 4.2434 | 9.8273 | 4.7519 | -51.646 | 126.3 | 145.47 | 15.177 | 4.2434 | 51.646 | 15.177
|  | F | 1.99 | 3.903 | 96.126 | 4.773 | 4.5654 | -4.348 | 128.9 | 112.25 | -12.92 | 96.126 | 4.348 | 12.92
|  | G33 | 5.9679 | 4.3407 | -27.265 |  |  |  | 106.6 | 138.22 | 29.662 | 27.265 |  | 29.662
| Test 8 | B | 2.9117 | 4.1378 | 42.111 | 5.5839 | 4.5785 | -18.006 | 183.31 | 142 | -22.535 | 42.111 | 18.006 | 22.535
|  | D | 3.5529 | 4.286 | 20.635 | 8.5136 | 4.7163 | -44.603 | 149.63 | 143.53 | -4.0769 | 20.635 | 44.603 | 4.0769
|  | F | 1.931 | 3.856 | 99.685 | 4.927 | 4.5268 | -8.1241 | 131.4 | 110.95 | -15.559 | 99.685 | 8.1241 | 15.559
|  | G33 | 6.0252 | 4.2945 | -28.724 | 5.98 | 4.6571 | -22.122 | 106.86 | 136.42 | 27.663 | 28.724 | 22.122 | 27.663
| Test 4 | B | 2.9162 | 3.859 | 32.328 | 5.5227 | 4.1411 | -25.017 | 148.76 | 155.53 | 4.548 | 32.328 | 25.017 | 4.548
|  | D | 3.255 | 3.9958 | 22.759 | 7.2296 | 4.2705 | -40.931 | 113.13 | 156.78 | 38.582 | 22.759 | 40.931 | 38.582
|  | F | 2.0227 | 3.6031 | 78.13 | 5.0236 | 4.1579 | -17.233 | 148.55 | 115.26 | -22.411 | 78.13 | 17.233 | 22.411
|  | G33 | 5.9962 | 3.9824 | -33.584 | 6.4245 | 4.2281 | -34.189 | 124.93 | 148.54 | 18.897 | 33.584 | 34.189 | 18.897
| Test 10 | B | 2.6898 | 3.8373 | 42.657 | 4.9052 | 4.0796 | -16.831 | 143.76 | 161.74 | 12.507 | 42.657 | 16.831 | 12.507
|  | D | 2.913 | 3.9729 | 36.387 | 6.7148 | 4.2052 | -37.375 | 132.45 | 163.53 | 23.469 | 36.387 | 37.375 | 23.469
|  | F | 1.9278 | 3.5834 | 85.88 | 4.3612 | 4.0372 | -7.4289 | 150.46 | 128.55 | -14.559 | 85.88 | 7.4289 | 14.559
|  | G33 | 5.4241 | 3.9598 | -26.995 | 6.2034 | 4.2012 | -32.276 | 148.3 | 148.87 | 0.38491 | 26.995 | 32.276 | 0.38491
| Test 13 | B | 4.7724 | 7.6938 | 61.213 | 8.2647 | 8.4281 | 1.9775 | 185.88 | 164.68 | -11.404 | 61.213 | 1.9775 | 11.404
|  | D | 6.5796 | 7.9837 | 21.341 | 11.221 | 8.6912 | -22.546 | 173.4 | 168.37 | -2.8974 | 21.341 | 22.546 | 2.8974
|  | F | 2.8973 | 7.1425 | 146.52 | 7.2846 | 8.0455 | 10.445 | 143.38 | 142.65 | -0.50947 | 146.52 | 10.445 | 0.50947
|  | G33 | 10.063 | 7.9967 | -20.533 | 12.176 | 8.5561 | -29.729 | 133.32 | 163.96 | 22.986 | 20.533 | 29.729 | 22.986
| Test 16 | B | 4.1167 | 6.5385 | 58.828 | 8.3662 | 7.1471 | -14.572 | 160.45 | 165.29 | 3.0167 | 58.828 | 14.572 | 3.0167
|  | D | 4.832 | 6.8064 | 40.862 | 11.666 | 7.3846 | -36.698 | 155.88 | 169.63 | 8.8196 | 40.862 | 36.698 | 8.8196
|  | F | 2.7579 | 6.0351 | 118.83 | 6.1349 | 6.7754 | 10.441 | 168.47 | 147.4 | -12.509 | 118.83 | 10.441 | 12.509
|  | G33 | 11.963 | 6.7876 | -43.264 | 12.228 | 7.3336 | -40.028 | 169.15 | 149.79 | -11.441 | 43.264 | 40.028 | 11.441
| Test 17 | B | 1.299 | 2.0804 | 60.158 | 2.3621 | 2.5837 | 9.3833 |  |  |  | 60.158 | 9.3833
|  | D | 1.5215 | 2.2011 | 44.666 | 3.2863 | 2.6865 | -18.25 |  |  |  | 44.666 | 18.25
|  | F | 0.88131 | 1.8561 | 110.61 | 1.852 | 2.4061 | 29.919 |  |  |  | 110.61 | 29.919
|  | G33 | 2.4164 | 2.2961 | -4.9785 | 3.0662 | 2.6604 | -13.234 |  |  |  | 4.9785 | 13.234
| Test 3 | B | 4.4473 | 4.8761 | 9.6435 | 7.103 | 4.9384 | -30.475 | 225.93 | 221.37 | -2.0181 | 9.6435 | 30.475 | 2.0181
|  | D |  |  |  | 9.4539 | 5.1082 | -45.967 | 209.68 | 222.55 | 6.1348 |  | 45.967 | 6.1348
|  | F | 2.9529 | 4.5264 | 53.289 | 5.5485 | 4.9039 | -11.617 | 195.36 | 159.54 | -18.336 | 53.289 | 11.617 | 18.336
|  | G33 | 5.3629 | 5.4724 | 2.0413 | 6.4501 | 5.5111 | -14.559 | 168.72 | 224.18 | 32.874 | 2.0413 | 14.559 | 32.874
| Test 9 | B | 4.2937 | 4.6838 | 9.0858 | 6.5843 | 4.7498 | -27.862 | 227.5 | 218.02 | -4.1648 | 9.0858 | 27.862 | 4.1648
|  | D | 5.2581 | 4.8549 | -7.6691 | 9.0579 | 4.9162 | -45.725 | 220.4 | 219.21 | -0.53902 | 7.6691 | 45.725 | 0.53902
|  | F | 2.7315 | 4.338 | 58.815 | 5.08 | 4.7243 | -7.0029 | 194.6 | 156.22 | -19.724 | 58.815 | 7.0029 | 19.724
|  | G33 | 5.1547 | 5.2786 | 2.4035 | 6.3723 | 5.3196 | -16.52 | 166.4 | 220.94 | 32.779 | 2.4035 | 16.52 | 32.779
| Test 5 | B | 3.8843 | 3.605 | -7.1896 | 6.8597 | 3.647 | -46.835 | 150.34 | 182.79 | 21.58 | 7.1896 | 46.835 | 21.58
|  | D | 4.7816 | 3.7432 | -21.716 | 8.5151 | 3.7799 | -55.609 | 132.39 | 184.24 | 39.164 | 21.716 | 55.609 | 39.164
|  | F | 2.6462 | 3.3154 | 25.289 | 6.4487 | 3.6386 | -43.575 | 174.88 | 127.91 | -26.858 | 25.289 | 43.575 | 26.858
|  | G33 | 5.4464 | 4.22 | -22.518 | 6.6852 | 4.2338 | -36.669 | 161 | 190.26 | 18.175 | 22.518 | 36.669 | 18.175
| Test 14 | B | 2.8398 | 4.1451 | 45.967 | 3.8193 | 4.2643 | 11.652 | 199 | 206.71 | 3.8734 | 45.967 | 11.652 | 3.8734
|  | D |  |  |  | 6.0732 | 4.4282 | -27.087 | 178.3 | 207.77 | 16.528 |  | 27.087 | 16.528
|  | F | 2.1188 | 3.8779 | 83.024 | 3.4636 | 4.3476 | 25.522 | 171.2 | 144.81 | -15.417 | 83.024 | 25.522 | 15.417
|  | G33 | 10.501 | 7.2915 | -30.566 | 10.901 | 7.2528 | -33.467 | 269.9 | 261.9 | -2.9655 | 30.566 | 33.467 | 2.9655
| Test 15 | B | 46.487 | 3.8823 | -91.649 | 57.721 | 4.0022 | -93.066 | 415.57 | 207.01 | -50.186 | 91.649 | 93.066 | 50.186
|  | D |  |  |  | 20.872 | 4.161 | -80.065 | 243.37 | 208.74 | -14.231 |  | 80.065 | 14.231
|  | F | 18.287 | 3.6167 | -80.223 | 23.944 | 4.0277 | -83.179 | 669.41 | 154.81 | -76.873 | 80.223 | 83.179 | 76.873
|  | G33 | 3.7305 | 7.0608 | 89.271 | 5.124 | 7.0182 | 36.969 | 161.06 | 263.34 | 63.508 | 89.271 | 36.969 | 63.508
| Test 18 | B | 5.2342 | 5.1001 | -2.5628 | 7.6097 | 5.1401 | -32.454 | 235.69 | 227.05 | -3.6649 | 2.5628 | 32.454 | 3.6649
|  | D |  |  |  | 7.8345 | 5.0065 | -36.096 | 217.21 | 221.5 | 1.9761 |  | 36.096 | 1.9761
|  | F | 5.1808 | 5.708 | 10.177 | 8.7351 | 5.9157 | -32.277 | 231.5 | 188.15 | -18.726 | 10.177 | 32.277 | 18.726
|  | G33 | 2.8461 | 4.3872 | 54.147 | 4.4495 | 4.4939 | 0.99739 |  |  |  | 54.147 | 0.99739
iBMB Pool | Test 1 | WS 2 |  |  |  | 27.18 | 36.532 | 34.409 | 356 | 359.67 | 1.0314 |  | 34.409 | 1.0314
|  | WS 3 |  |  |  | 46.555 | 37.269 | -19.945 | 308.15 | 412.79 | 33.959 |  | 19.945 | 33.959
|  | WS 4 |  |  |  | 32.413 | 35.759 | 10.325 | 489.15 | 514 | 5.08 |  | 10.325 | 5.08
iBMB Cable | Test 4 | WS 2 / TCO 1-3 |  |  |  | 2.91 | 1.62 | -44.332 | 87.22 | 66.342 | -23.937 |  | 44.332 | 23.937
|  | TCO 2-3 | [6 empty] | 111.68 | 84.905 | -23.975 |  |  | 23.975
|  | WS 3 / TCO 1-5 |  |  |  | 96.68 | 2.1556 | -97.77 | 109.75 | 87.23 | -20.519 |  | 97.77 | 20.519
|  | TCO 2-5 | [6 empty] | 146.25 | 114.15 | -21.951 |  |  | 21.951
|  | WS 4 / TCO 1-7 |  |  |  | 5.75 | 2.1542 | -62.536 | 106.69 | 87.154 | -18.311 |  | 62.536 | 18.311
|  | TCO 2-7 | [6 empty] | 140.25 | 113.13 | -19.335 |  |  | 19.335
Average ----> |  |  |  |  | 26.724 |  |  | -22.6995 |  |  | -0.14523 | 42.7754 | 29.284 | 18.1771
Standard Deviation ----> |  |  |  |  | 47.8291 |  |  | 28.2458 |  |  | 23.6767 | 33.938 | 21.2137 | 14.9956
Median ----> |  |  |  |  | 23.682 |  |  | -22.122 |  |  | -2.8974 | 34.9855 | 27.087 | 17.84
Percentile ranking at uncertainty limit ----> | [11 empty] | 0.252 | 0.419 | 0.384
90th percentile value ----> | [11 empty] | 90.46 | 50.6838 | 33.742

## Surface Flux and Temperature
Absolute Values
|  |  | Total Flux to Surface |  |  | Surface Temperature |  |  | Flux | Temp
Series | Test | Measurement Position | Exp | CFAST | Relative Difference | Exp | CFAST | Relative Difference | Relative Difference | Relative Difference
|  |  | (kW/m2) | (kW/m2) | (%) | (°C) | (°C) | (%) | (%) | (%)
NIST / NRC | Test 1 | Long Wall | 1.3849 | 1.6716 | 20.708 | 54.2 | 88.945 | 64.105 | 20.708 | 64.105
|  |  | 1.7657 | 1.6525 | -6.4115 | 68 | 88.994 | 30.874 | 6.4115 | 30.874
|  | Short Wall | 1.2583 | 1.6706 | 32.767 | 55.4 | 88.51 | 59.765 | 32.767 | 59.765
|  |  | 1.7222 | 1.6669 | -3.2117 | 71 | 89.118 | 25.518 | 3.2117 | 25.518
|  | Floor | 0.92441 | 1.3695 | 48.145 | 38.2 | 70.94 | 85.706 | 48.145 | 85.706
|  |  | 2.3828 | 1.3363 | -43.92 | 77.4 | 69.214 | -10.576 | 43.92 | 10.576
|  | Ceiling | 1.9286 | 1.7032 | -11.684 | 80.7 | 91.93 | 13.916 | 11.684 | 13.916
|  |  | 3.7541 | 1.6687 | -55.55 | 176.3 | 90.61 | -48.605 | 55.55 | 48.605
| Test 7 | Long Wall | 1.379 | 1.6397 | 18.902 | 53.134 | 86.5 | 62.795 | 18.902 | 62.795
|  |  | 1.8768 | 1.6196 | -13.704 | 70.29 | 86.57 | 23.162 | 13.704 | 23.162
|  | Short Wall | 1.2216 | 1.6403 | 34.277 | 54.624 | 86.122 | 57.664 | 34.277 | 57.664
|  |  | 1.7871 | 1.6349 | -8.5166 | 70.155 | 86.704 | 23.59 | 8.5166 | 23.59
|  | Floor | 0.90253 | 1.3406 | 48.542 | 36.357 | 68.635 | 88.782 | 48.542 | 88.782
|  |  | 2.3194 | 1.3078 | -43.614 | 78.206 | 66.936 | -14.412 | 43.614 | 14.412
|  | Ceiling | 1.9418 | 1.6704 | -13.977 | 79.891 | 89.487 | 12.011 | 13.977 | 12.011
[6 empty] | 191.41 | 88.149 | -53.946 |  | 53.946
| Test 2 | Long Wall | 3.775 | 4.4026 | 16.627 | 95.6 | 150.35 | 57.266 | 16.627 | 57.266
|  |  | 4.5124 | 4.3435 | -3.7422 | 120.1 | 151.34 | 26.014 | 3.7422 | 26.014
|  | Short Wall | 3.6207 | 4.397 | 21.44 | 109.6 | 149.77 | 36.651 | 21.44 | 36.651
|  |  | 4.62 | 4.3911 | -4.9545 | 125.4 | 150.61 | 20.102 | 4.9545 | 20.102
|  | Floor | 2.5919 | 3.6517 | 40.892 | 74.2 | 127.01 | 71.166 | 40.892 | 71.166
|  |  | 8.9025 | 3.5445 | -60.186 | 156.2 | 123.53 | -20.915 | 60.186 | 20.915
|  | Ceiling | 5.6472 | 4.4656 | -20.923 | 147.8 | 154.15 | 4.293 | 20.923 | 4.293
|  |  | 14.507 | 4.3415 | -70.073 | 308.2 | 152.01 | -50.678 | 70.073 | 50.678
| Test 8 | Long Wall | 3.8377 | 4.363 | 13.688 | 94.561 | 148.58 | 57.126 | 13.688 | 57.126
|  |  | 3.2551 | 4.3027 | 32.186 | 131.97 | 149.86 | 13.554 | 32.186 | 13.554
|  | Short Wall | 2.4635 | 4.3574 | 76.878 | 109.05 | 147.98 | 35.701 | 76.878 | 35.701
|  |  | 4.6996 | 4.3514 | -7.4083 | 124.67 | 148.84 | 19.386 | 7.4083 | 19.386
|  | Floor | 2.5552 | 3.6042 | 41.057 | 71.211 | 125.18 | 75.78 | 41.057 | 75.78
|  |  | 8.6335 | 3.4969 | -59.496 | 148.16 | 121.54 | -17.968 | 59.496 | 17.968
|  | Ceiling | 6.1416 | 4.4273 | -27.913 | 147.82 | 152.53 | 3.1841 | 27.913 | 3.1841
|  |  | 12.923 | 4.3021 | -66.709 | 325.27 | 150.56 | -53.712 | 66.709 | 53.712
| Test 4 | Long Wall | 3.4102 | 3.9546 | 15.965 | 96.934 | 149.61 | 54.344 | 15.965 | 54.344
|  |  | 3.5068 | 3.9523 | 12.701 | 145.5 | 151.51 | 4.1264 | 12.701 | 4.1264
|  | Short Wall | 3.2605 | 3.9493 | 21.127 | 105.81 | 149.18 | 40.989 | 21.127 | 40.989
|  |  | 3.9741 | 3.9457 | -0.71463 | 120.85 | 149.69 | 23.86 | 0.71463 | 23.86
|  | Floor | 2.4658 | 3.3261 | 34.891 | 76.361 | 129.75 | 69.919 | 34.891 | 69.919
|  |  | 8.5108 | 3.2435 | -61.89 | 151.7 | 126.84 | -16.384 | 61.89 | 16.384
|  | Ceiling | 5.0838 | 4.0064 | -21.191 | 147.25 | 152.89 | 3.8265 | 21.191 | 3.8265
|  |  | 6.0192 | 3.9623 | -34.172 | 180.03 | 152.67 | -15.2 | 34.172 | 15.2
| Test 10 | Long Wall | 3.3458 | 3.9315 | 17.506 | 93.967 | 149.75 | 59.36 | 17.506 | 59.36
|  |  | 3.4816 | 3.9295 | 12.864 | 162.69 | 151.39 | -6.9488 | 12.864 | 6.9488
|  | Short Wall | 3.1225 | 3.9301 | 25.861 | 105.68 | 149.44 | 41.407 | 25.861 | 41.407
|  |  | 3.8794 | 3.9227 | 1.1159 | 117.19 | 149.84 | 27.855 | 1.1159 | 27.855
|  | Floor | 2.2749 | 3.3052 | 45.288 | 71.047 | 129.65 | 82.487 | 45.288 | 82.487
|  |  | 7.8927 | 3.2236 | -59.158 | 157.89 | 126.74 | -19.729 | 59.158 | 19.729
|  | Ceiling | 4.7915 | 3.9828 | -16.878 | 137.86 | 152.96 | 10.952 | 16.878 | 10.952
[6 empty] | 221.12 | 152.55 | -31.007 |  | 31.007
| Test 13 | Long Wall |  |  |  | 110.36 | 194.7 | 76.411 |  | 76.411
[6 empty] | 199.43 | 197.84 | -0.79612 |  | 0.79612
|  | Short Wall |  |  |  | 126.58 | 193.88 | 53.162 |  | 53.162
[6 empty] | 144.91 | 195.3 | 34.772 |  | 34.772
|  | Floor |  |  |  | 89.208 | 166 | 86.083 |  | 86.083
[6 empty] | 148.76 | 160.85 | 8.1248 |  | 8.1248
|  | Ceiling |  |  |  | 319.28 | 196.23 | -38.54 |  | 38.54
[6 empty] | 498.07 | 196.62 | -60.523 |  | 60.523
| Test 16 | Long Wall |  |  |  | 106.85 | 175.1 | 63.874 |  | 63.874
[6 empty] | 217.13 | 179.81 | -17.188 |  | 17.188
|  | Short Wall |  |  |  | 123.22 | 174.44 | 41.565 |  | 41.565
[6 empty] | 141.16 | 175.28 | 24.169 |  | 24.169
|  | Floor |  |  |  | 80.012 | 147.78 | 84.692 |  | 84.692
[6 empty] | 145.87 | 143.28 | -1.7709 |  | 1.7709
|  | Ceiling |  |  |  | 283.68 | 177.65 | -37.378 |  | 37.378
[6 empty] | 441.38 | 179.19 | -59.402 |  | 59.402
| Test 17 | Long Wall | 1.4618 | 2.1086 | 44.244 | 39.006 | 52.895 | 35.609 | 44.244 | 35.609
|  |  | 0.92901 | 2.2775 | 145.15 | 82.059 | 65.248 | -20.487 | 145.15 | 20.487
|  | Short Wall | 1.5595 | 2.1062 | 35.06 | 56.478 | 51.569 | -8.6931 | 35.06 | 8.6931
|  |  | 1.899 | 2.0973 | 10.443 | 61.024 | 54.038 | -11.448 | 10.443 | 11.448
|  | Floor | 0.85627 | 1.3776 | 60.881 | 24.436 | 34.11 | 39.589 | 60.881 | 39.589
|  |  | 1.4991 | 1.3235 | -11.714 | 51.919 | 32.526 | -37.353 | 11.714 | 37.353
|  | Ceiling |  |  |  | 68.643 | 57.735 | -15.891 |  | 15.891
[6 empty] | 229.79 | 64.352 | -71.995 |  | 71.995
| Test 3 | Long Wall | 3.4986 | 4.4532 | 27.284 | 114.33 | 187.23 | 63.767 | 27.284 | 63.767
|  |  | 4.3205 | 5.0084 | 15.92 | 172.39 | 202.94 | 17.726 | 15.92 | 17.726
|  | Short Wall | 2.5288 | 3.5956 | 42.185 | 87.285 | 152.2 | 74.374 | 42.185 | 74.374
|  |  | 4.446 | 4.5805 | 3.0235 | 145.78 | 190.95 | 30.986 | 3.0235 | 30.986
|  | Floor | 1.9712 | 3.1937 | 62.018 | 53.598 | 142.73 | 166.29 | 62.018 | 166.29
|  |  | 4.0716 | 3.0854 | -24.222 | 118.69 | 138.6 | 16.78 | 24.222 | 16.78
|  | Ceiling | 4.6169 | 4.6603 | 0.93814 | 155.21 | 194.16 | 25.097 | 0.93814 | 25.097
|  |  | 9.8764 | 4.7752 | -51.651 | 287.38 | 197.41 | -31.306 | 51.651 | 31.306
| Test 9 | Long Wall | 3.4162 | 4.2672 | 24.911 | 112.9 | 183.61 | 62.631 | 24.911 | 62.631
|  |  | 4.2045 | 4.8213 | 14.671 | 177.9 | 199.78 | 12.3 | 14.671 | 12.3
|  | Short Wall | 2.418 | 3.4245 | 41.623 | 88.1 | 147.9 | 67.879 | 41.623 | 67.879
[6 empty] | 134.9 | 187.59 | 39.055 |  | 39.055
|  | Floor | 1.9116 | 3.0359 | 58.815 | 53.1 | 138.73 | 161.26 | 58.815 | 161.26
|  |  | 3.8865 | 2.9301 | -24.608 | 121.8 | 134.56 | 10.479 | 24.608 | 10.479
|  | Ceiling | 5.4505 | 4.4642 | -18.097 | 203.6 | 190.55 | -6.4077 | 18.097 | 6.4077
|  |  | 9.4103 | 4.5899 | -51.225 | 289.9 | 194.23 | -33.002 | 51.225 | 33.002
| Test 5 | Long Wall | 2.6847 | 3.0679 | 14.273 | 93.718 | 145.67 | 55.435 | 14.273 | 55.435
|  |  | 3.8129 | 3.7265 | -2.2663 | 154.56 | 168.06 | 8.7326 | 2.2663 | 8.7326
|  | Short Wall | 1.9983 | 2.5357 | 26.895 | 71.394 | 115.78 | 62.172 | 26.895 | 62.172
|  |  | 3.2917 | 3.1221 | -5.1516 | 117.59 | 147.88 | 25.756 | 5.1516 | 25.756
|  | Floor | 1.3997 | 2.1874 | 56.274 | 41.655 | 106.86 | 156.53 | 56.274 | 156.53
|  |  | 10.055 | 2.1351 | -78.766 | 170.76 | 104.33 | -38.905 | 78.766 | 38.905
|  | Ceiling | 3.3715 | 3.1846 | -5.5434 | 125.27 | 151.15 | 20.663 | 5.5434 | 20.663
|  |  | 6.7402 | 3.414 | -49.349 | 263.41 | 158.77 | -39.726 | 49.349 | 39.726
| Test 14 | Long Wall | 3.4995 | 4.3033 | 22.97 | 114.4 | 184.23 | 61.038 | 22.97 | 61.038
|  |  | 8.1035 | 5.6733 | -29.99 | 254.7 | 221.9 | -12.879 | 29.99 | 12.879
|  | Short Wall | 2.3515 | 3.5088 | 49.214 | 86.8 | 148.96 | 71.613 | 49.214 | 71.613
|  |  | 4.4708 | 4.4613 | -0.21263 | 147.6 | 188.92 | 27.995 | 0.21263 | 27.995
|  | Floor | 1.8926 | 3.0998 | 63.788 | 52.2 | 140.67 | 169.48 | 63.788 | 169.48
|  |  | 2.969 | 2.9942 | 0.85055 | 103.8 | 136.55 | 31.554 | 0.85055 | 31.554
|  | Ceiling | 4.6945 | 4.5419 | -3.2516 | 157.7 | 192.22 | 21.89 | 3.2516 | 21.89
|  |  | 8.9935 | 4.8348 | -46.241 | 351.8 | 200.39 | -43.039 | 46.241 | 43.039
| Test 15 | Long Wall | 3.6352 | 4.0693 | 11.944 | 219.66 | 183.29 | -16.556 | 11.944 | 16.556
|  |  | 7.4632 | 4.2069 | -43.631 | 205.45 | 187.59 | -8.6951 | 43.631 | 8.6951
|  | Short Wall | 2.6102 | 3.2579 | 24.814 | 96.276 | 144.87 | 50.475 | 24.814 | 50.475
|  |  | 4.6546 | 4.1944 | -9.8865 | 151.44 | 187.21 | 23.619 | 9.8865 | 23.619
|  | Floor | 1.9485 | 2.8519 | 46.362 | 52.299 | 136.56 | 161.12 | 46.362 | 161.12
|  |  | 5.2316 | 2.7506 | -47.424 | 131.58 | 132.36 | 0.59248 | 47.424 | 0.59248
|  | Ceiling |  |  |  | 156.87 | 190.75 | 21.602 |  | 21.602
[6 empty] | 287.15 | 186.12 | -35.184 |  | 35.184
| Test 18 | Long Wall | 3.4041 | 4.2703 | 25.446 | 118.16 | 184.63 | 56.248 | 25.446 | 56.248
[6 empty] | 312.36 | 248.3 | -20.507 |  | 20.507
|  | Short Wall | 2.5826 | 3.5242 | 36.46 | 94.013 | 154.22 | 64.043 | 36.46 | 64.043
|  |  | 4.6654 | 4.4936 | -3.6835 | 152.9 | 190.34 | 24.491 | 3.6835 | 24.491
|  | Floor | 1.7895 | 3.1074 | 73.651 | 49.57 | 141.32 | 185.09 | 73.651 | 185.09
|  |  | 3.0569 | 3.0031 | -1.7599 | 106.6 | 137.25 | 28.76 | 1.7599 | 28.76
|  | Ceiling | 4.4785 | 4.5494 | 1.583 | 144.9 | 192.93 | 33.144 | 1.583 | 33.144
[6 empty] | 250.11 | 193.63 | -22.58 |  | 22.58
iBMB Pool | Test 1 | M 19 |  |  |  | 595.74 | 546.19 | -8.3179 |  | 8.3179
|  | M 20 |  |  |  | 721.67 | 237.94 | -67.029 |  | 67.029
iBMB Cable | Test 4 | TW 1-1 |  |  |  | 55.9 | 36.563 | -34.592 |  | 34.592
|  | TW 2-1 |  |  |  | 4.41 | 23.912 | 442.23 |  | 442.23
|  | TW 1-4 |  |  |  | 87.35 | 36.217 | -58.538 |  | 58.538
|  | TW 2-4 |  |  |  | 68.02 | 34.71 | -48.971 |  | 48.971
|  | TW 1-7 |  |  |  | 86.16 | 36.927 | -57.141 |  | 57.141
|  | TW 2-7 |  |  |  | 71.81 | 36.686 | -48.912 |  | 48.912
Average ----> |  |  |  |  | 4.7416 |  |  | 24.3309 | 30.5241 | 45.797
Standard Deviation ----> |  |  |  |  | 38.8425 |  |  | 63.4785 | 24.2864 | 50.1227
Median ----> |  |  |  |  | 1.583 |  |  | 21.746 | 24.911 | 34.978
Percentile ranking at uncertainty limit ----> | [8 empty] | 0.4 | 0.174
90th percentile value ----> | [8 empty] | 60.603 | 75.9693