## CompareList
NRC Comparisons
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
Experiment | FM_SNL_Test_4_Exp | 2
Model | FM_SNL_Test_4_Mod | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 3 | 1 | 2 | 0 | 15 | Max
Compare | HGL Height | HGL Height | 1 | 2 | 1 | 3 | 0 | 15 | Min | Closed |  | 6.1 |  |  | 6.1
Compare | Temperature 1/0.98H | Ceiling Jet Temperature | 5 | 6 | 1 | 9 | 0 | 15 | Max
Compare | Temperature 11/0.98H | Ceiling Jet Temperature | 5 | 16 | 1 | 8 | 0 | 15 | Max
Compare | Temperature 28/0.98H | Plume Temperature | 5 | 21 | 1 | 10 | 0 | 15 | Max
Experiment | FM_SNL_Test_5_Exp | 2
Model | FM_SNL_Test_5_Mod | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 3 | 1 | 2 | 0 | 15 | Max
Compare | HGL Height | HGL Height | 1 | 2 | 1 | 3 | 0 | 15 | Min | Closed |  | 6.1 |  |  | 6.1
Compare | Temperature 1/0.98H | Ceiling Jet Temperature | 5 | 6 | 1 | 9 | 0 | 15 | Max
Compare | Temperature 11/0.98H | Ceiling Jet Temperature | 5 | 16 | 1 | 8 | 0 | 15 | Max
Compare | Temperature 28/0.98H | Plume Temperature | 5 | 21 | 1 | 10 | 0 | 15 | Max
Experiment | FM_SNL_Test_21_Exp | 2
Model | FM_SNL_Test_21_Mod | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 3 | 1 | 2 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 2 | 1 | 3 | 0 | 30 | Min | Closed |  | 6.1 |  |  | 6.1
Compare | Temperature 1/0.98H | Ceiling Jet Temperature | 5 | 6 | 1 | 9 | 0 | 30 | Max
Compare | Temperature 11/0.98H | Ceiling Jet Temperature | 5 | 16 | 1 | 8 | 0 | 30 | Max
Compare | Temperature 6/0.98H | Plume Temperature | 5 | 11 | 1 | 10 | 0 | 30 | Max
Experiment | ICFMP2_Case_1 | 2
Model | ICFMP2_Case_1 | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 83 | 34 | 35 | 0 | 8 | Max
Compare | HGL Height | HGL Height | 1 | 81 | 34 | 36 | 0 | 8 | Min | Closed |  | 19 |  |  | 19
Compare | Temperature TG.1 | Plume Temperature | 1 | 32 | 34 | 41 | 0 | 8 | Max
Compare | Temperature TG.2 | Plume Temperature | 1 | 33 | 34 | 42 | 0 | 8 | Max
Experiment | ICFMP2_Case_2 | 3
Model | ICFMP2_Case_2 | 3
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 4 | 8 | 9 | 0 | 8 | Max
Compare | HGL Height | HGL Height | 1 | 2 | 8 | 10 | 0 | 8 | Min | Closed |  | 19 |  |  | 19
Compare | Temperature TG.1 | Plume Temperature | 1 | 5 | 8 | 15 | 0 | 8 | Max
Compare | Temperature TG.2 | Plume Temperature | 1 | 6 | 8 | 16 | 0 | 8 | Max
Experiment | ICFMP2_Case_3 | 2
Model | ICFMP2_Case_3 | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 48 | 35 | 36 | 0 | 8 | Max
Compare | HGL Height | HGL Height | 1 | 46 | 35 | 37 | 0 | 8 | Min |  |  | 19 |  |  | 19
Compare | Temperature TG.1 | Plume Temperature | 1 | 32 | 35 | 42 | 0 | 8 | Max
Compare | Temperature TG.2 | Plume Temperature | 1 | 33 | 35 | 43 | 0 | 8 | Max
Experiment | ICFMP3_Test_1 | 1
Model | ICFMP3_Test_1 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | [14 empty] | No experimental measurement
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | [14 empty] | No experimental measurement
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | [14 empty] | No experimental measurement
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max
Experiment | ICFMP3_Test_2 | 1
Model | ICFMP3_Test_2 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 342 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | [14 empty] | No experimental measurement
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 365 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max
Experiment | ICFMP3_Test_3 | 1
Model | ICFMP3_Test_3 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | [14 empty] | No experimental measurement
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max
Experiment | ICFMP3_Test_4 | 1
Model | ICFMP3_Test_4 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 342 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 354 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max
Experiment | ICFMP3_Test_5 | 1
Model | ICFMP3_Test_5 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 354 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | 0 | 30 | Max
Experiment | ICFMP3_Test_7 | 1
Model | ICFMP3_Test_7 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 342 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 365 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372
Experiment | ICFMP3_Test_8 | 1
Model | ICFMP3_Test_8 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 354 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max
Experiment | ICFMP3_Test_9 | 1
Model | ICFMP3_Test_9 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 139 | 325 | 346 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 166 | 325 | 348 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 17 | 325 | 369 | [14 empty] | No experimental measurement
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 31 | 325 | 371 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max
Experiment | ICFMP3_Test_10 | 1
Model | ICFMP3_Test_10 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372
Experiment | ICFMP3_Test_13 | 1
Model | ICFMP3_Test_13 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 139 | 325 | 346 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 177 | 325 | 351 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | [14 empty] | No experimental measurement
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | [14 empty] | No experimental measurement
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | [14 empty] | No experimental measurement
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 369 | [14 empty] | No experimental measurement
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | [14 empty] | No experimental measurement
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | [14 empty] | No experimental measurement
Compare | Ceiling 1 Flux | Surface Flux | 1 | 36 | 325 | 374 | [14 empty] | No experimental measurement
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | [14 empty] | No experimental measurement
Experiment | ICFMP3_Test_14 | 1
Model | ICFMP3_Test_14 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max | [11 empty] | No experimental measurement
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | 0 | 30 | Max
Experiment | ICFMP3_Test_15 | 1
Model | ICFMP3_Test_15 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 125 | 325 | 340 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 124 | 325 | 341 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | [14 empty] | No experimental measurement
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 8 | 325 | 363 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 10 | 325 | 364 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372
Experiment | ICFMP3_Test_16 | 1
Model | ICFMP3_Test_16 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 177 | 325 | 351 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | [14 empty] | No experimental measurement
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | [14 empty] | No experimental measurement
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | [14 empty] | No experimental measurement
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | [14 empty] | No experimental measurement
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | [14 empty] | No experimental measurement
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | [14 empty] | No experimental measurement
Compare | Ceiling 1 Flux | Surface Flux | 1 | 36 | 325 | 374 | [14 empty] | No experimental measurement
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | [14 empty] | No experimental measurement
Experiment | ICFMP3_Test_17 | 1
Model | ICFMP3_Test_17 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | [14 empty] | No experimental measurement
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | [14 empty] | No experimental measurement
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | [14 empty] | No experimental measurement
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | [14 empty] | No experimental measurement
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | [14 empty] | No experimental measurement
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | [14 empty] | No experimental measurement
Experiment | ICFMP3_Test_18 | 1
Model | ICFMP3_Test_18 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 |  |  | 3.82
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 |  |  | 0
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 |  |  | 0
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max | [11 empty] | No experimental measurement
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 121 | 325 | 338 | 0 | 30 | Max
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 342 | 0 | 30 | Max
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 343 | 0 | 30 | Max
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | [14 empty] | No experimental measurement
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max
Compare | Long Wall 1 Flux | Surface Flux | 1 | 8 | 325 | 363 | 0 | 30 | Max
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 365 | [14 empty] | No experimental measurement
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | [14 empty] | No experimental measurement
Experiment | ICFMP4_Test_1 | 1
Model | ICFMP4_Test_1 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 117 | 136 | 1 | 2 | 0 | 30 | Max
Compare | HGL Height | HGL Height | 117 | 138 | 1 | 3 | 0 | 20 | Min |  |  | 5.7 |  |  | 5.7
Compare | Steel Heat Flux | Surface Temperature | 117 | 186 | 1 | 11 | 0 | 30 | Max
Compare | Concrete Heat Flux | Surface Temperature | 117 | 187 | 1 | 13 | 0 | 30 | Max
Compare | Light Concrete Heat Flux | Surface Temperature | 117 | 188 | 1 | 15 | 0 | 30 | Max
Compare | Steel Heat Temperature | Surface Flux | 117 | 156 | 1 | 10 | 0 | 30 | Max
Compare | Concrete Heat Temperature | Surface Flux | 117 | 155 | 1 | 12 | 0 | 30 | Max
Compare | Light Concrete Heat Temperature | Surface Flux | 117 | 151 | 1 | 14 | 0 | 30 | Max
Compare | M19 Temperature | Surface Temperature | 117 | 139 | 1 | 16 | 0 | 30 | Max
Compare | M20 Temperature | Surface Temperature | 117 | 140 | 1 | 17 | 0 | 30 | Max
Experiment | ICFMP5_Test_4 | 1
Model | ICFMP5_Test_4 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 125 | 168 | 1 | 2 | 0 | 20 | Max
Compare | HGL Height | HGL Height | 125 | 170 | 1 | 3 | 5 | 20 | Min |  |  | 5.6 |  |  | 5.6
Compare | Oxygen | Oxygen | 125 | 293 | 1 | 5 | 0 | 20 | Min
Compare | Carbon Dioxide | Carbon Dioxide | 125 | 295 | 1 | 6 | 0 | 20 | Max
Compare | WS2 Flux | Cable Flux | 125 | 271 | 1 | 11 | 0 | 20 | Max
Compare | WS 3 Flux | Cable Flux | 125 | 172 | 1 | 13 | 0 | 20 | Max |  |  | 0
Compare | WS 4 Flux | Cable Flux | 125 | 273 | 1 | 15 | 0 | 20 | Max
Compare | TCO 1-3 Temperature | Cable Temperature | 125 | 199 | 1 | 18 | 0 | 20 | Max
Compare | TCO 1-5 Temperature | Cable Temperature | 125 | 201 | 1 | 19 | 0 | 20 | Max
Compare | TCO 1-7 Temperature | Cable Temperature | 125 | 203 | 1 | 20 | 0 | 20 | Max
Compare | TCO 3-3 Temperature | Cable Temperature | 125 | 217 | 1 | 21 | 0 | 20 | Max
Compare | TCO 3-5 Temperature | Cable Temperature | 125 | 219 | 1 | 22 | 0 | 20 | Max
Compare | TCO 3-7 Temperature | Cable Temperature | 125 | 221 | 1 | 23 | 0 | 20 | Max |  | -7
Compare | TW 1-1 Temperature | Surface Temperature | 125 | 171 | 1 | 24 | 0 | 20 | Max
Compare | TW 1-4 Temperature | Surface Temperature | 125 | 174 | 1 | 25 | 0 | 20 | Max
Compare | TW 1-7 Temperature | Surface Temperature | 125 | 177 | 1 | 26 | 0 | 20 | Max
Compare | TW 2-1 Temperature | Surface Temperature | 125 | 178 | 1 | 27 | 0 | 20 | Max
Compare | TW 2-4 Temperature | Surface Temperature | 125 | 181 | 1 | 28 | 0 | 20 | Max
Compare | TW 2-7 Temperature | Surface Temperature | 125 | 184 | 1 | 29 | 0 | 20 | Max
Experiment | MV100A | 1
Model | MV100A | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Tree 1 HGL Temperature | HGL Temperature | 271 | 275 | 257 | 258 | 5 | 15 | Max |  |  | 23
Compare | Tree 1 HGL Height | HGL Height | 271 | 273 | 257 | 259 | 5 | 15 | Min |  |  | 2.16 |  |  | 2.16
Compare | Tree 4 HGL Temperature | HGL Temperature | 271 | 279 | 257 | 264 | 5 | 15 | Max |  |  | 23
Compare | Tree 4 HGL Height | HGL Height | 271 | 277 | 257 | 265 | 5 | 15 | Min |  |  | 2.44 |  |  | 2.44
Compare | Tree 5 HGL Temperature | HGL Temperature | 271 | 283 | 257 | 266 | 5 | 15 | Max |  |  | 23
Compare | Tree 5 HGL Height | HGL Height | 271 | 281 | 257 | 267 | 5 | 15 | Min |  |  | 2.44 |  |  | 2.44
Compare | Tree 6 HGL Temperature | HGL Temperature | 271 | 287 | 257 | 268 | 5 | 15 | Max |  |  | 23
Compare | Tree 6 HGL Height | HGL Height | 271 | 285 | 257 | 269 | 5 | 15 | Min |  |  | 2.44 |  |  | 2.44
Experiment | MV100O | 1
Model | MV100O | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Tree 1 HGL Temperature | HGL Temperature | 280 | 284 | 266 | 267 | 5 | 15 | Max |  |  | 21
Compare | Tree 1 HGL Height | HGL Height | 280 | 282 | 266 | 268 | 5 | 15 | Min | Closed |  | 2.16 |  |  | 2.16
Compare | Tree 4 HGL Temperature | HGL Temperature | 280 | 288 | 266 | 273 | 5 | 15 | Max |  |  | 21
Compare | Tree 4 HGL Height | HGL Height | 280 | 286 | 266 | 274 | 5 | 15 | Min | Closed |  | 2.44 |  |  | 2.44
Compare | Tree 5 HGL Temperature | HGL Temperature | 280 | 292 | 266 | 275 | 5 | 15 | Max |  |  | 21
Compare | Tree 5 HGL Height | HGL Height | 280 | 290 | 266 | 276 | 5 | 15 | Min | Closed |  | 2.44 |  |  | 2.44
Compare | Tree 6 HGL Temperature | HGL Temperature | 280 | 296 | 266 | 277 | [5 empty] | 21 | [8 empty] | No experimental measurement
Compare | Tree 6 HGL Height | HGL Height | 280 | 294 | 266 | 278 | 5 | 15 | Min | Closed
Experiment | MV100Z | 1
Model | MV100Z | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Tree 1 HGL Temperature | HGL Temperature | 331 | 335 | 313 | 314 | 5 | 15 | Max |  |  | 22 | [8 empty] | Experimental Peak = 282
Compare | Tree 1 HGL Height | HGL Height | 331 | 333 | 313 | 315 | 5 | 15 | Min |  |  | 2.16 |  |  | 2.16 | [5 empty] | Experimental Peak = 1.0
Compare | Tree 4 HGL Temperature | HGL Temperature | 331 | 339 | 313 | 320 | 5 | 15 | Max |  |  | 22
Compare | Tree 4 HGL Height | HGL Height | 331 | 337 | 313 | 321 | 5 | 15 | Min |  |  | 2.44 |  |  | 2.44
Compare | Tree 5 HGL Temperature | HGL Temperature | 331 | 343 | 313 | 322 | 5 | 15 | Max |  |  | 22
Compare | Tree 5 HGL Height | HGL Height | 331 | 341 | 313 | 323 | 5 | 15 | Min |  |  | 2.44 |  |  | 2.44
Compare | Tree 7 HGL Temperature | HGL Temperature | 331 | 347 | 313 | 328 | 5 | 15 | Max |  |  | 22
Compare | Tree 7 HGL Height | HGL Height | 331 | 345 | 313 | 329 | 5 | 15 | Min |  |  | 2.43 |  |  | 2.43
Experiment | NIST_Plaza | 3
Model | NIST_Plaza | 3
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Burn Room HGL Temperature | HGL Temperature | 1 | 2 | 10 | 11 | 0 | 30 | Max
Compare | Burn Room HGL Height | HGL Height | 1 | [17 empty] | No experimental measurement
Compare | Corridor HGL Temperature | HGL Temperature | 1 | 3 | 10 | 12 | 0 | 30 | Max
Compare | Corridor HGL Height | HGL Height | 1 | [17 empty] | No experimental measurement
Compare | Floor 7 HGL Temperature | HGL Temperature | 1 | 7 | 10 | 16 | 0 | 30 | Max
Compare | Floor 7 HGL Height | HGL Height | 1 | [17 empty] | No experimental measurement
Compare | Corridor Oxygen | Oxygen | 1 | 4 | 10 | 13 | 0 | 30 | Min
Compare | Corridor Carbon Dioxide | Carbon Dioxide | 1 | 6 | 10 | 15 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Corridor 7 Pressure | Pressure | 1 | 8 | 10 | 17 | 0 | 30 | Max
Experiment | fm19 | 5
Model | fm19 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 123 | 114 | 126 | 127 | 0 | 8 | Max
Compare | Room 1 HGL Height | HGL Height | 123 | 14 | 126 | 128 | 0 | 8 | Min |  |  | 2.45
Compare | Room 1 Oxygen | Oxygen | 123 | 20 | 126 | 130 | 0 | 8 | Min
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 123 | 2 | 126 | 131 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 123 |  | 126 | 129 | [14 empty] | No experimental measurement
Compare | Room 2 HGL Temperature | HGL Temperature | 123 | 115 | 126 | 132 | 0 | 8 | Max
Compare | Room 2 HGL Height | HGL Height | 123 | 11 | 126 | 133 | 0 | 8 | Min |  |  | 2.43
Compare | Room 2 HGL Temperature | HGL Temperature | 123 | 116 | 126 | 132 | 0 | 8 | Max
Compare | Room 2 HGL Height | HGL Height | 123 | 12 | 126 | 133 | 0 | 8 | Min |  |  | 2.43
Compare | Room 2 HGL Temperature | HGL Temperature | 123 | 117 | 126 | 132 | 0 | 8 | Max
Compare | Room 2 HGL Height | HGL Height | 123 | 13 | 126 | 133 | 0 | 8 | Min |  |  | 2.43
Compare | Room 2 Oxygen | Oxygen | 123 | 19 | 126 | 135 | 0 | 8 | Min
Compare | Room 2 Carbon Dioxide | Carbon Dioxide | 123 | 1 | 126 | 136 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 2 Pressure | Pressure | 123 |  | 126 | 134 | [14 empty] | No experimental measurement
Compare | Room 3 HGL Temperature | HGL Temperature | 123 | 118 | 126 | 137 | 0 | 8 | Max
Compare | Room 3 HGL Height | HGL Height | 123 | 15 | 126 | 138 | 0 | 8 | Min |  |  | 2.45
Compare | Room 3 Carbon Dioxide | Carbon Dioxide | 123 | 3 | 126 | 141 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 3 Pressure | Pressure | 123 |  | 126 | 139 | [14 empty] | No experimental measurement
Compare | Room 4 HGL Temperature | HGL Temperature | 123 | 119 | 126 | 142 | 0 | 8 | Max
Compare | Room 4 HGL Height | HGL Height | 123 | 16 | 126 | 143 | 0 | 8 | Min |  |  | 2.43
Compare | Room 4 Carbon Dioxide | Carbon Dioxide | 123 | 4 | 126 | 146 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 4 Pressure | Pressure | 123 |  | 126 | 144 | [14 empty] | No experimental measurement
Experiment | fm21 | 5
Model | fm21 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 125 | 116 | 128 | 129 | 0 | 8 | Max
Compare | Room 1 HGL Height | HGL Height | 125 | 16 | 128 | 130 | 0 | 8 | Min |  |  | 2.45
Compare | Room 1 Oxygen | Oxygen | 125 | 22 | 128 | 132 | 0 | 8 | Min
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 125 | 4 | 128 | 133 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 125 |  | 128 | 131 | [14 empty] | No experimental measurement
Compare | Room 2 HGL Temperature | HGL Temperature | 125 | 117 | 128 | 134 | 0 | 8 | Max
Compare | Room 2 HGL Height | HGL Height | 125 | 13 | 128 | 135 | 0 | 8 | Min |  |  | 2.43
Compare | Room 2 HGL Temperature | HGL Temperature | 125 | 118 | 128 | 134 | 0 | 8 | Max
Compare | Room 2 HGL Height | HGL Height | 125 | 14 | 128 | 135 | 0 | 8 | Min |  |  | 2.43
Compare | Room 2 HGL Temperature | HGL Temperature | 125 | 119 | 128 | 134 | 0 | 8 | Max
Compare | Room 2 HGL Height | HGL Height | 125 | 15 | 128 | 135 | 0 | 8 | Min |  |  | 2.43
Compare | Room 2 Oxygen | Oxygen | 125 | 21 | 128 | 137 | 0 | 8 | Min
Compare | Room 2 Carbon Dioxide | Carbon Dioxide | 125 | 1 | 128 | 138 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 2 Carbon Dioxide | Carbon Dioxide | 125 | 2 | 128 | 138 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 2 Pressure | Pressure | 125 |  | 128 | 136 | [14 empty] | No experimental measurement
Compare | Room 3 HGL Temperature | HGL Temperature | 125 | 120 | 128 | 139 | 0 | 8 | Max
Compare | Room 3 HGL Height | HGL Height | 125 | 17 | 128 | 140 | 0 | 8 | Min |  |  | 2.45
Compare | Room 3 Carbon Dioxide | Carbon Dioxide | 125 | 5 | 128 | 143 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 3 Pressure | Pressure | 125 |  | 128 | 141 | [14 empty] | No experimental measurement
Compare | Room 4 HGL Temperature | HGL Temperature | 125 | 120 | 128 | 144 | 0 | 8 | Max
Compare | Room 4 HGL Height | HGL Height | 125 | 18 | 128 | 145 | 0 | 8 | Min |  |  | 2.43
Compare | Room 4 Carbon Dioxide | Carbon Dioxide | 125 | 6 | 128 | 148 | 0 | 8 | Max |  |  | 0 |  |  | 0
Compare | Room 4 Pressure | Pressure | 125 |  | 128 | 146 | [14 empty] | No experimental measurement
Experiment | 1Room1 | 5
Model | 1Room1 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature A | HGL Temperature | 87 | 85 | 109 | 110 | 0 | 30 | Max
Compare | Room 1 HGL Height A | HGL Height | 87 | 11 | 109 | 111 | 0 | 30 | Min |  |  | 2.31
Compare | Room 1 HGL Temperature B | HGL Temperature | 87 | 86 | 109 | 110 | 0 | 30 | Max
Compare | Room 1 HGL Height B | HGL Height | 87 | 12 | 109 | 111 | 0 | 30 | Min |  |  | 2.31
Compare | Room 1 Oxygen A | Oxygen | 87 | 21 | 109 | 113 | 0 | 30 | Min
Compare | Room 1 Carbon Dioxide A | Carbon Dioxide | 87 | 3 | 109 | 114 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Room 1 Oxygen B | Oxygen | 87 | 22 | 109 | 113 | 0 | 30 | Min
Compare | Room 1 Carbon Dioxide B | Carbon Dioxide | 87 | 4 | 109 | 114 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 87 |  | 109 | 112 | [14 empty] | No experimental measurement
Experiment | 1Room6 | 5
Model | 1Room6 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature A | HGL Temperature | 87 | 85 | 113 | 114 | 0 | 30 | Max
Compare | Room 1 HGL Height A | HGL Height | 87 | 11 | 113 | 115 | 0 | 30 | Min |  |  | 2.31
Compare | Room 1 HGL Temperature B | HGL Temperature | 87 | 86 | 113 | 114 | 0 | 30 | Max
Compare | Room 1 HGL Height B | HGL Height | 87 | 12 | 113 | 115 | 0 | 30 | Min |  |  | 2.31
Compare | Room 1 Oxygen A | Oxygen | 87 | 21 | 113 | 117 | 0 | 30 | Min
Compare | Room 1 Carbon Dioxide A | Carbon Dioxide | 87 | 3 | 113 | 118 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Room 1 Oxygen B | Oxygen | 87 | 22 | 113 | 117 | 0 | 30 | Min
Compare | Room 1 Carbon Dioxide B | Carbon Dioxide | 87 | 4 | 113 | 118 | 0 | 30 | Max |  |  | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 87 |  | 113 | 116 | [14 empty] | No experimental measurement
Experiment | 1RWall1 | 5
Model | 1RWall1 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 83 | 82 | 110 | 111 | 0 | 30 | Max
Compare | Room 1 HGL Height | HGL Height | 83 | 8 | 110 | 112 | 0 | 30 | Min |  |  | 2.44
Compare | Room 1 Oxygen | Oxygen | 83 |  | 110 | 114
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 83 |  | 110 | 115 | [5 empty] | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 83 | 32 | 110 | 113 | 0 | 30 | Min
Experiment | 1RWall2 | 5
Model | 1RWall2 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 105 | 104 | 133 | 134 | 0 | 10 | Max
Compare | Room 1 HGL Height | HGL Height | 105 | 8 | 133 | 135 | 0 | 10 | Min |  |  | 2.44
Compare | Room 1 Oxygen | Oxygen | 105 |  | 133 | 137
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 105 |  | 133 | 138 | [5 empty] | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 105 | 32 | 133 | 136 | 0 | 10 | Min
End

## Output
NRC Comparisons
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
Experiment | FM_SNL_Test_4_Exp | 2
Model | FM_SNL_Test_4_Mod | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 3 | 1 | 2 | 0 | 15 | Max |  |  | 12.7 | 71.7 | 10 | 15 | 83.938 | 10 | 59 | 68.938 | 16.845
Compare | HGL Height | HGL Height | 1 | 2 | 1 | 3 | 0 | 15 | Min | Closed |  | 6.1 | 2.6981 | 6.3333 | 6.1 | 0.57267 | 14.833 | -3.4019 | -5.5273
Compare | Temperature 1/0.98H | Ceiling Jet Temperature | 5 | 6 | 1 | 9 | 0 | 15 | Max |  |  | 16.4 | 98.58 | 10 | 15 | 148.49 | 10 | 82.18 | 133.49 | 62.436
Compare | Temperature 11/0.98H | Ceiling Jet Temperature | 5 | 16 | 1 | 8 | 0 | 15 | Max |  |  | 15.4 | 81.18 | 10 | 15 | 117.45 | 10 | 65.78 | 102.45 | 55.746
Compare | Temperature 28/0.98H | Plume Temperature | 5 | 21 | 1 | 10 | 0 | 15 | Max |  |  | 17.2 | 131.4 | 9.3333 | 15 | 152 | 10 | 114.2 | 137 | 19.968
Experiment | FM_SNL_Test_5 | 2
Model | FM_SNL_Test_5 | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 11 | 13 | 1 | 2 | 0 | 15 | Max |  |  | 21 | 65.223 | 10 | 20 | 69.21 | 10 | 44.223 | 49.21 | 11.277
Compare | HGL Height | HGL Height | 11 | 12 | 1 | 3 | 0 | 15 | Min | Closed |  | 6.1 | 3.1888 | 5.5 | 6.1 | 0.49275 | 13.167 | -2.9112 | -5.6073
Compare | Temperature 1/0.98H | Ceiling Jet Temperature | 15 | 16 | 1 | 9 | 0 | 15 | Max |  |  | 21.1 | 91.519 | 10 | 20 | 121 | 10 | 70.419 | 101 | 43.427
Compare | Temperature 11/0.98H | Ceiling Jet Temperature | 15 | 26 | 1 | 8 | 0 | 15 | Max |  |  | 20.6 | 73.16 | 10.167 | 20 | 95 | 10 | 52.56 | 75 | 42.694
Compare | Temperature 28/0.98H | Plume Temperature | 5 | 21 | 1 | 10 | 0 | 15 | Max |  |  | 21.2 | 114.6 | 9 | 20 | 132 | 10 | 93.402 | 112 | 19.911
Experiment | FM_SNL_Test_21 | 2
Model | FM_SNL_Test_21 | 2
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 11 | 13 | 1 | 2 | 0 | 30 | Max |  |  | 17.7 | 83.7 | 19 | 15 | 102.97 | 19 | 66 | 87.966 | 33.282
Compare | HGL Height | HGL Height | 11 | 12 | 1 | 3 | 0 | 30 | Min | Closed |  | 6.1 | 2.6707 | 7.1667 | 6.1 | 0.013373 | 29 | -3.4293 | -6.0866
Compare | Temperature 1/0.98H | Ceiling Jet Temperature | 15 | 16 | 1 | 9 | 0 | 30 | Max |  |  | 18.2 | 93.033 | 19.167 | 15 | 174 | 19 | 74.833 | 159 | 112.47
Compare | Temperature 11/0.98H | Ceiling Jet Temperature | 15 | 26 | 1 | 8 | 0 | 30 | Max |  |  | 17.2 | 94.1 | 19.167 | 15 | 139.3 | 19 | 76.9 | 124.3 | 61.644
Compare | Temperature 6/0.98H | Plume Temperature | 5 | 11 | 1 | 10 | 0 | 30 | Max |  |  | 17.2 | 96.2 | 18.5 | 15 | 201 | 19 | 79 | 186 | 135.44
Experiment | ICFMP2_Case_1 | 1
Model | ICFMP2_Case_1 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 83 | 34 | 35 | 0 | 8 | Max |  |  | 20.9 | 75.7 | 7 | 20 | 82.3 | 7 | 54.8 | 62.3 | 13.686
Compare | HGL Height | HGL Height | 1 | 81 | 34 | 36 | 0 | 8 | Min | Closed |  | 19 | 4.43 | 8 | 19 | 1.71 | 6.8333 | -14.57 | -17.29
Compare | Temperature TG.1 | Plume Temperature | 1 | 32 | 34 | 41 | 0 | 8 | Max |  |  | 17 | 183 | 6 | 20 | 194 | 6.8333 | 166 | 174 | 4.8193
Compare | Temperature TG.2 | Plume Temperature | 1 | 33 | 34 | 42 | 0 | 8 | Max |  |  | 19 | 96 | 6 | 20 | 125 | 7.6667 | 77 | 105 | 36.364
Experiment | ICFMP2_Case_2 | 1
Model | ICFMP2_Case_2 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 4 | 6 | 7 | 0 | 8 | Max |  |  | 23 | 109 | 6 | 20 | 119 | 6.1667 | 86 | 99 | 15.116
Compare | HGL Height | HGL Height | 1 | 2 | 6 | 8 | 0 | 8 | Min | Closed |  | 19 | 4.23 | 7 | 19 | 1.02 | 5.8333 | -14.77 | -17.98
Compare | Temperature TG.1 | Plume Temperature | 1 | 5 | 8 | 15 | 0 | 8 | Max |  |  | 20 | 308 | 5 | 20 | 264 | 6.3333 | 288 | 244 | -15.278
Compare | Temperature TG.2 | Plume Temperature | 1 | 6 | 8 | 16 | 0 | 8 | Max |  |  | 20 | 148 | 6 | 20 | 181 | 6.5 | 128 | 161 | 25.781
Experiment | ICFMP2_Case_3 | 1
Model | ICFMP2_Case_3 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 46 | 35 | 36 | 0 | 8 | Max |  |  | 22.5 | 105 | 5 | 20 | 111 | 5.5 | 82.5 | 91 | 10.303
Compare | HGL Height | HGL Height | 1 | 44 | 35 | 37 | 0 | 8 | Min |  |  | 19 | 5.14 | 5 | 19 | 4.06 | 4.5 | -13.86 | -14.94 | 7.7922
Compare | Temperature TG.1 | Plume Temperature | 1 | 32 | 35 | 42 | 0 | 8 | Max |  |  | 16 | 268 | 4 | 20 | 258 | 5.3333 | 252 | 238 | -5.5556
Compare | Temperature TG.2 | Plume Temperature | 1 | 33 | 35 | 43 | 0 | 8 | Max |  |  | 17 | 145 | 4 | 20 | 161 | 5.8333 | 128 | 141 | 10.156
Experiment | ICFMP3_Test_1 | 1
Model | ICFMP3_Test_1 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 20.9 | 143.83 | 22.833 | 22 | 157.48 | 22.667 | 122.93 | 135.48 | 10.207
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.78 | 27.333 | 3.82 | 0.0071329 | 22.5 | -3.04 | -3.8129
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 20.1 | 174.67 | 22.667 | 22 | 157.48 | 22.667 | 154.57 | 135.48 | -12.348
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.144 | 23.833 | 0.20535 | 0.12924 | 24.667 | -0.065 | -0.076111 | 17.094
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.0384 | 24.5 | 0 | 0.044428 | 24.833 | 0.0384 | 0.044428 | 15.697
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 41.467 | 26.833 | 0 | 320.45 | 30 | 41.467 | 320.45 | 672.79
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 57.522 | 3.1667 | 0 | 42.398 | 2.5 | 57.522 | 42.398 | -26.292
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 23.6 | 130 | 23.833 | 22 | 124.77 | 23.833 | 106.4 | 102.77 | -3.4107
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | [14 empty] | No experimental measureme
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 23.4 | 106 | 23.833 | 22 | 89.853 | 23.333 | 82.6 | 67.853 | -17.854
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 23.5 | 87.817 | 24.333 | 22 | 117.96 | 23.833 | 64.317 | 95.955 | 49.191
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 18.1 | 72.283 | 24.167 | 22 | 110.94 | 23.333 | 54.183 | 88.943 | 64.152
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 339 | 0 | 30 | Max |  |  | 19.9 | 87.867 | 23.167 | 22 | 110.99 | 23.167 | 67.967 | 88.993 | 30.936
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 17 | 72.317 | 24.333 | 22 | 110.51 | 23.333 | 55.317 | 88.512 | 60.009
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 17.3 | 88.25 | 23.167 | 22 | 111.12 | 23.333 | 70.95 | 89.118 | 25.607
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 17.2 | 55.4 | 24.5 | 22 | 92.94 | 23.167 | 38.2 | 70.94 | 85.708
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max |  |  | 18.2 | 95.583 | 22.833 | 22 | 91.215 | 23.167 | 77.383 | 69.215 | -10.556
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 21.3 | 102 | 22.667 | 22 | 113.93 | 23.333 | 80.7 | 91.93 | 13.916
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 22.7 | 198.83 | 22.333 | 22 | 112.61 | 23.167 | 176.13 | 90.611 | -48.555
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.00297 | 1.8417 | 21.833 | 0 | 2.46 | 22.5 | 1.8446 | 2.46 | 33.359
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | [14 empty] | No experimental measureme
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.0157 | 1.6083 | 19.667 | 0 | 2.37 | 22.5 | 1.5926 | 2.37 | 48.81
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | [14 empty] | No experimental measureme
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.00149 | 1.1183 | 22.667 | 0 | 2.32 | 22.5 | 1.1198 | 2.32 | 107.18
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | -0.00936 | 1.43 | 22.5 | 0 | 1.5 | 22.167 | 1.4394 | 1.5 | 4.2131
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | 0.00108 | 0.86767 | 22.667 | 0 | 1.36 | 22.333 | 0.86659 | 1.36 | 56.938
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.00106 | 1.5083 | 21.667 | 0 | 1.51 | 22.5 | 1.5094 | 1.51 | 0.040232
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | -0.0144 | 1.37 | 23.167 | 0 | 1.96 | 22.333 | 1.3844 | 1.96 | 41.578
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 362 | 0 | 30 | Max |  |  | -0.00564 | 1.76 | 22.5 | 0 | 1.95 | 22.5 | 1.7656 | 1.95 | 10.442
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max |  |  | -0.00505 | 1.25 | 22.5 | 0 | 1.96 | 22.333 | 1.255 | 1.96 | 56.169
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | -0.0178 | 1.7 | 23 | 0 | 1.96 | 22.333 | 1.7178 | 1.96 | 14.1
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | -0.0264 | 0.898 | 23.5 | 0 | 1.68 | 22.5 | 0.9244 | 1.68 | 81.74
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | -0.00771 | 2.38 | 11.5 | 0 | 1.65 | 22.5 | 2.3877 | 1.65 | -30.896
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | -0.0144 | 1.91 | 22.167 | 0 | 2.21 | 22.5 | 1.9244 | 2.21 | 14.841
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max |  |  | 0.0348 | 3.7883 | 22.667 | 0 | 2.17 | 22.333 | 3.7535 | 2.17 | -42.188
Experiment | ICFMP3_Test_2 | 1
Model | ICFMP3_Test_2 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 24 | 253 | 10 | 26 | 260.57 | 10.333 | 229 | 234.57 | 2.4336
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.825 | 11.667 | 3.82 | 0.011216 | 10.333 | -2.995 | -3.8088
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 23.4 | 293.86 | 9.8333 | 26 | 260.57 | 10.333 | 270.46 | 234.57 | -13.27
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.11667 | 10.333 | 0.20471 | 0.10423 | 10.333 | -0.092333 | -0.10048 | 8.8264
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.05455 | 10.333 | 0 | 0.058654 | 10.333 | 0.05455 | 0.058654 | 7.5225
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 128 | 8.1667 | 0 | 419.47 | 20.167 | 128 | 419.47 | 227.71
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 290 | 2 | 0 | 266.05 | 3 | 290 | 266.05 | -8.2593
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 26.3 | 201.67 | 10.333 | 26 | 169.98 | 10.333 | 175.37 | 143.98 | -17.898
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 26.7 | 151 | 10.167 | 26 | 171.47 | 10.333 | 124.3 | 145.47 | 17.033
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 26.1 | 154.67 | 10.333 | 26 | 138.25 | 10.333 | 128.57 | 112.25 | -12.69
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 26.4 | 133 | 10.5 | 26 | 164.22 | 10.333 | 106.6 | 138.22 | 29.665
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 21.4 | 116.83 | 10.667 | 26 | 176.35 | 10.5 | 95.433 | 150.35 | 57.546
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 342 | 0 | 30 | Max |  |  | 22.9 | 143 | 10.333 | 26 | 177.35 | 10.333 | 120.1 | 151.35 | 26.02
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 20.4 | 129.83 | 10.667 | 26 | 175.77 | 10.5 | 109.43 | 149.77 | 36.862
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 20.6 | 146 | 10.333 | 26 | 176.61 | 10.5 | 125.4 | 150.61 | 20.106
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 20.7 | 94.783 | 10.833 | 26 | 153.01 | 10.333 | 74.083 | 127.01 | 71.445
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max |  |  | 21.8 | 178 | 7.6667 | 26 | 149.54 | 10.333 | 156.2 | 123.54 | -20.911
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 24.2 | 172 | 10.333 | 26 | 180.15 | 10.5 | 147.8 | 154.15 | 4.2977
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 25.8 | 333.69 | 9.8333 | 26 | 178.02 | 10.333 | 307.89 | 152.02 | -50.625
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.000495 | 5.2512 | 9.8333 | 0 | 5.77 | 10.333 | 5.2517 | 5.77 | 9.8698
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.0373 | 9.2769 | 9.8333 | 0 | 5.91 | 10.333 | 9.3142 | 5.91 | -36.548
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.00705 | 4.6867 | 10.167 | 0 | 5.51 | 10.333 | 4.6796 | 5.51 | 17.745
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | [14 empty] | No experimental measureme
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.00241 | 2.8794 | 7.1667 | 0 | 5.37 | 10.333 | 2.8818 | 5.37 | 86.34
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.00379 | 4.03 | 10.167 | 0 | 4.12 | 10.333 | 4.0262 | 4.12 | 2.3294
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -4.71e-05 | 1.9867 | 10.167 | 0 | 3.71 | 10.333 | 1.9867 | 3.71 | 86.741
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | 0.00213 | 5.9694 | 4.6667 | 0 | 4.12 | 10.333 | 5.9673 | 4.12 | -30.957
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.0209 | 3.8 | 10.5 | 0 | 4.65 | 10.333 | 3.7791 | 4.65 | 23.045
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 365 | 0 | 30 | Max |  |  | 0.0287 | 4.5333 | 10.167 | 0 | 4.61 | 10.333 | 4.5046 | 4.61 | 2.3391
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max |  |  | 0.0313 | 3.62 | 9.5 | 0 | 4.64 | 10.333 | 3.5887 | 4.64 | 29.295
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.0196 | 4.63 | 10.167 | 0 | 4.64 | 10.333 | 4.6104 | 4.64 | 0.64202
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.0111 | 2.59 | 10.333 | 0 | 4.17 | 10.333 | 2.5789 | 4.17 | 61.697
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | 0.0295 | 8.9282 | 6.6667 | 0 | 4.06 | 10.333 | 8.8987 | 4.06 | -54.376
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.0221 | 5.67 | 10 | 0 | 5.08 | 10.333 | 5.6479 | 5.08 | -10.055
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max |  |  | 0.0626 | 14.541 | 9.8333 | 0 | 4.97 | 10.333 | 14.479 | 4.97 | -65.673
Experiment | ICFMP3_Test_3 | 1
Model | ICFMP3_Test_3 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 27.8 | 235 | 23.167 | 30 | 273 | 22.667 | 207.2 | 243 | 17.278
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 | 0.91 | 21 | 3.82 | 1.01 | 3.5 | -2.91 | -2.81 | -3.4364
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 27.1 | 267.5 | 22.833 | 30 | 273 | 22.667 | 240.4 | 243 | 1.0814
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.157 | 23.167 | 0.204 | 0.16 | 10.333 | -0.052 | -0.044 | -15.385
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.0311 | 11.833 | 0 | 0.0273 | 11.833 | 0.0311 | 0.0273 | -12.219
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 117.5 | 21.667 | 0 | 140 | 10.167 | 117.5 | 140 | 19.149
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 | -1.91 | 26 | 0 | -2.1 | 23.5 | -1.91 | -2.1 | 9.948
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 30 | 256 | 23.333 | 30 | 251 | 23.167 | 226 | 221 | -2.2124
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 30.9 | 240.83 | 24.333 | 30 | 253 | 23.333 | 209.93 | 223 | 6.2241
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 30.1 | 225 | 23.667 | 30 | 190 | 23.333 | 194.9 | 160 | -17.907
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 30 | 199 | 24.167 | 30 | 254 | 23.167 | 169 | 224 | 32.544
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 26.4 | 141 | 24.167 | 30 | 217 | 23.167 | 114.6 | 187 | 63.176
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 26 | 198 | 23.333 | 30 | 233 | 23.167 | 172 | 203 | 18.023
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 24.1 | 111 | 23.333 | 30 | 182 | 23 | 86.9 | 152 | 74.914
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 24.4 | 170 | 23.833 | 30 | 221 | 23.167 | 145.6 | 191 | 31.181
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 25.1 | 78.7 | 24.5 | 30 | 173 | 23.333 | 53.6 | 143 | 166.79
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 24.7 | 143 | 23.333 | 30 | 169 | 23.333 | 118.3 | 139 | 17.498
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 29.5 | 184.83 | 24.167 | 30 | 224 | 23.167 | 155.33 | 194 | 24.893
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 28.9 | 316 | 23.5 | 30 | 227 | 22.833 | 287.1 | 197 | -31.383
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.0124 | 7.08 | 20.833 | 0 | 6.48 | 23 | 7.0924 | 6.48 | -8.6346
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.0136 | 9.4399 | 22 | 0 | 6.65 | 23 | 9.4535 | 6.65 | -29.656
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.0152 | 5.4917 | 20.667 | 0 | 6.15 | 23 | 5.5069 | 6.15 | 11.679
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.0232 | 6.4233 | 22.333 | 0 | 6.6 | 23 | 6.4465 | 6.6 | 2.3806
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.00103 | 4.44 | 23.167 | 0 | 5.64 | 23 | 4.441 | 5.64 | 26.998
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | [14 empty] | No experimental measureme
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.00034 | 2.945 | 23.167 | 0 | 4.3 | 23 | 2.9453 | 4.3 | 45.993
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | 0.00111 | 5.3557 | 3.6667 | 0 | 5.2 | 23 | 5.3546 | 5.2 | -2.8868
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.0731 | 3.5683 | 21.833 | 0 | 4.83 | 23 | 3.4952 | 4.83 | 38.188
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.0679 | 4.3867 | 23.667 | 0 | 5.32 | 23 | 4.3188 | 5.32 | 23.183
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max |  |  | 0.0726 | 2.6 | 23.5 | 0 | 3.48 | 23 | 2.5274 | 3.48 | 37.691
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.0577 | 4.5 | 23 | 0 | 4.94 | 23 | 4.4423 | 4.94 | 11.204
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.0609 | 2.0283 | 23.167 | 0 | 3.58 | 23 | 1.9674 | 3.58 | 81.963
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max |  |  | 0.0614 | 4.11 | 23.167 | 0 | 3.46 | 23 | 4.0486 | 3.46 | -14.538
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.075 | 4.6617 | 22.167 | 0 | 5.43 | 23 | 4.5867 | 5.43 | 18.387
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max |  |  | 0.101 | 9.8634 | 22.333 | 0 | 5.54 | 23 | 9.7624 | 5.54 | -43.252
Experiment | ICFMP3_Test_4 | 1
Model | ICFMP3_Test_4 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 24.8 | 229 | 13.333 | 27 | 249 | 13.5 | 204.2 | 222 | 8.7169
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.565 | 19.833 | 3.82 | 0.0178 | 13.5 | -3.255 | -3.8022
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 23.8 | 251.5 | 12.833 | 27 | 249 | 13.5 | 227.7 | 222 | -2.5033
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.131 | 13.833 | 0.204 | 0.144 | 13.333 | -0.078 | -0.06 | -23.077
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.04735 | 13.833 | 0 | 0.035 | 13.5 | 0.04735 | 0.035 | -26.082
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 79.892 | 8.3333 | 0 | 177 | 13.333 | 79.892 | 177 | 121.55
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 56.6 | 1.5 | 0 | 76.8 | 3 | 56.6 | 76.8 | 35.689
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 26.2 | 174.17 | 13.667 | 27 | 183 | 13.5 | 147.97 | 156 | 5.429
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 26.2 | 138.83 | 13.667 | 27 | 184 | 13.5 | 112.63 | 157 | 39.39
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 25.9 | 173.83 | 13.667 | 27 | 142 | 13.5 | 147.93 | 115 | -22.262
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 26.3 | 150.83 | 13.667 | 27 | 176 | 13.5 | 124.53 | 149 | 19.647
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 21.7 | 118.83 | 13.667 | 27 | 177 | 13.5 | 97.133 | 150 | 54.427
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 342 | 0 | 30 | Max |  |  | 22.7 | 168 | 13.5 | 27 | 179 | 13.5 | 145.3 | 152 | 4.6112
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 20.2 | 126 | 13.5 | 27 | 176 | 13.5 | 105.8 | 149 | 40.832
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 20.4 | 141 | 13.5 | 27 | 177 | 13.5 | 120.6 | 150 | 24.378
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 20.4 | 96.683 | 13.667 | 27 | 157 | 13.5 | 76.283 | 130 | 70.417
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 354 | 0 | 30 | Max |  |  | 21.4 | 173 | 13.333 | 27 | 154 | 13.5 | 151.6 | 127 | -16.227
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 24.5 | 171.67 | 13.667 | 27 | 180 | 13.5 | 147.17 | 153 | 3.9637
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 24.9 | 205 | 12.5 | 27 | 180 | 13.5 | 180.1 | 153 | -15.047
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.0328 | 5.49 | 13 | 0 | 5.36 | 13.5 | 5.5228 | 5.36 | -2.9476
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.102 | 7.13 | 12.5 | 0 | 5.49 | 13.5 | 7.232 | 5.49 | -24.087
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.0597 | 5.08 | 12.5 | 0 | 5.12 | 13.5 | 5.0203 | 5.12 | 1.9861
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.197 | 6.1967 | 13.167 | 0 | 5.07 | 13.5 | 6.3937 | 5.07 | -20.703
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | 0.00264 | 2.9117 | 12.333 | 0 | 4.96 | 13.5 | 2.909 | 4.96 | 70.504
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.00268 | 3.255 | 12.333 | 0 | 3.8 | 13.5 | 3.2523 | 3.8 | 16.84
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.000937 | 2.02 | 13.5 | 0 | 3.43 | 13.5 | 2.0209 | 3.43 | 69.724
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | 0.000338 | 5.9982 | 7.1667 | 0 | 3.79 | 13.5 | 5.9979 | 3.79 | -36.811
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.0264 | 3.4317 | 13.167 | 0 | 4.25 | 13.5 | 3.4053 | 4.25 | 24.807
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.0339 | 3.54 | 13.5 | 0 | 4.26 | 13.5 | 3.5061 | 4.26 | 21.503
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max |  |  | 0.034 | 3.29 | 13.5 | 0 | 4.25 | 13.5 | 3.256 | 4.25 | 30.529
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.0209 | 4 | 13.5 | 0 | 4.25 | 13.5 | 3.9791 | 4.25 | 6.8082
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.0104 | 2.4783 | 13.333 | 0 | 3.89 | 13.5 | 2.4679 | 3.89 | 57.622
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | 0.0336 | 8.54 | 7 | 0 | 3.8 | 13.5 | 8.5064 | 3.8 | -55.328
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.0273 | 5.07 | 12.667 | 0 | 4.66 | 13.5 | 5.0427 | 4.66 | -7.5893
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max |  |  | 0.0608 | 6.0782 | 3.1667 | 0 | 4.63 | 13.5 | 6.0174 | 4.63 | -23.057
Experiment | ICFMP3_Test_5 | 1
Model | ICFMP3_Test_5 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 25 | 200.83 | 23.167 | 28 | 226 | 22.667 | 175.83 | 198 | 12.607
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 | 0.87166 | 28.833 | 3.82 | 1.16 | 3.8333 | -2.9483 | -2.66 | -9.7796
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 23.6 | 230.67 | 21.333 | 28 | 226 | 22.667 | 207.07 | 198 | -4.3787
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.179 | 14.333 | 0.204 | 0.178 | 7.3333 | -0.03 | -0.026 | -13.333
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.0175 | 6.5 | 0 | 0.0161 | 8.5 | 0.0175 | 0.0161 | -7.9999
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 87.033 | 22.167 | 0 | 90.6 | 7.8333 | 87.033 | 90.6 | 4.0982
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 | -1.81 | 25.5 | 0 | -1.96 | 23.667 | -1.81 | -1.96 | 8.2882
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 26.7 | 176.33 | 23.667 | 28 | 211 | 23.167 | 149.63 | 183 | 22.299
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 26.5 | 159 | 23.833 | 28 | 212 | 23 | 132.5 | 184 | 38.868
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 26.3 | 201 | 23.333 | 28 | 156 | 23 | 174.7 | 128 | -26.732
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 26.9 | 188 | 23.833 | 28 | 218 | 23 | 161.1 | 190 | 17.939
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 23.3 | 117 | 23.333 | 28 | 174 | 23.167 | 93.7 | 146 | 55.816
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 23.6 | 178 | 23.333 | 28 | 196 | 22.833 | 154.4 | 168 | 8.8083
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 21.6 | 92.717 | 21.333 | 28 | 144 | 23.167 | 71.117 | 116 | 63.112
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 21.5 | 139 | 23.333 | 28 | 176 | 23.167 | 117.5 | 148 | 25.957
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 22.3 | 63.9 | 24 | 28 | 135 | 23.167 | 41.6 | 107 | 157.21
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 354 | 0 | 30 | Max |  |  | 22 | 193 | 23.333 | 28 | 132 | 23 | 171 | 104 | -39.181
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 26.1 | 151 | 22.833 | 28 | 179 | 23 | 124.9 | 151 | 20.897
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max |  |  | 25.8 | 289 | 23.167 | 28 | 187 | 23.167 | 263.2 | 159 | -39.59
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.062 | 6.7367 | 20.167 | 0 | 4.93 | 23 | 6.7987 | 4.93 | -27.486
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.153 | 8.34 | 22.333 | 0 | 5.06 | 23 | 8.493 | 5.06 | -40.422
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.0765 | 6.53 | 21 | 0 | 4.65 | 23 | 6.4535 | 4.65 | -27.946
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.109 | 6.58 | 22 | 0 | 5.15 | 23 | 6.689 | 5.15 | -23.008
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.00149 | 3.88 | 21 | 0 | 4.05 | 22.833 | 3.8815 | 4.05 | 4.3414
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | -0.00557 | 4.765 | 19.833 | 0 | 3.56 | 23 | 4.7706 | 3.56 | -25.376
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | 0.00158 | 2.64 | 23.167 | 0 | 3.15 | 22.833 | 2.6384 | 3.15 | 19.39
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | 0.000386 | 5.45 | 23 | 0 | 4.01 | 22.833 | 5.4496 | 4.01 | -26.417
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.0446 | 2.72 | 23.333 | 0 | 3.46 | 23 | 2.6754 | 3.46 | 29.326
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.0436 | 3.86 | 23 | 0 | 4.06 | 23 | 3.8164 | 4.06 | 6.383
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max |  |  | 0.0459 | 2.0267 | 21.167 | 0 | 2.48 | 23 | 1.9808 | 2.48 | 25.204
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.0284 | 3.32 | 23.5 | 0 | 3.51 | 23 | 3.2916 | 3.51 | 6.6353
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.033 | 1.4283 | 23.333 | 0 | 2.48 | 23 | 1.3953 | 2.48 | 77.735
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | 0.0492 | 10.061 | 7.1667 | 0 | 2.41 | 22.833 | 10.011 | 2.41 | -75.927
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.0446 | 3.4033 | 22.667 | 0 | 3.9 | 23 | 3.3587 | 3.9 | 16.115
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | 0 | 30 | Max |  |  | 0.0696 | 6.81 | 23 | 0 | 4.11 | 22.833 | 6.7404 | 4.11 | -39.024
Experiment | ICFMP3_Test_7 | 1
Model | ICFMP3_Test_7 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 22.2 | 139 | 22.333 | 24 | 157 | 22.333 | 116.8 | 133 | 13.87
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.77 | 25.667 | 3.82 | 0.0072 | 22.167 | -3.05 | -3.8128
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 21.6 | 160.67 | 22.333 | 24 | 157 | 22.333 | 139.07 | 133 | -4.3625
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.145 | 23.333 | 0.204 | 0.131 | 23.167 | -0.064 | -0.073 | 14.062
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.037983 | 23.167 | 0 | 0.0426 | 23.667 | 0.037983 | 0.0426 | 12.154
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 55.05 | 27.833 | 0 | 307 | 29 | 55.05 | 307 | 457.67
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 45.882 | 2.8333 | 0 | 28.8 | 2.1667 | 45.882 | 28.8 | -37.231
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 24.5 | 134 | 22.833 | 24 | 126 | 22.667 | 109.5 | 102 | -6.8493
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 25.3 | 113 | 22.833 | 24 | 126 | 22.5 | 87.7 | 102 | 16.306
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 23.9 | 114 | 22.833 | 24 | 97.3 | 22.667 | 90.1 | 73.3 | -18.646
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 24.1 | 102 | 22.667 | 24 | 117 | 22.667 | 77.9 | 93 | 19.384
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 19.1 | 72.2 | 23.667 | 24 | 111 | 22.833 | 53.1 | 87 | 63.842
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 342 | 0 | 30 | Max |  |  | 21 | 91.283 | 22.833 | 24 | 111 | 22.667 | 70.283 | 87 | 23.785
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max |  |  | 18.2 | 72.767 | 23.833 | 24 | 110 | 22.333 | 54.567 | 86 | 57.605
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 18.5 | 88.683 | 22.833 | 24 | 111 | 22.667 | 70.183 | 87 | 23.961
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 18.3 | 54.6 | 22.833 | 24 | 92.6 | 22.5 | 36.3 | 68.6 | 88.981
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max |  |  | 19.4 | 97.567 | 22.667 | 24 | 90.9 | 22.5 | 78.167 | 66.9 | -14.414
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 22.6 | 103 | 22.5 | 24 | 113.33 | 22.833 | 80.4 | 89.333 | 11.111
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 23.7 | 215 | 21 | 24 | 112 | 22.167 | 191.3 | 88 | -53.999
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.0038 | 1.8383 | 22.833 | 0 | 2.4 | 22.167 | 1.8421 | 2.4 | 30.284
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.0488 | 2.47 | 22.5 | 0 | 2.4467 | 22.167 | 2.5188 | 2.4467 | -2.8634
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.00705 | 1.4933 | 20.833 | 0 | 2.31 | 22.167 | 1.5004 | 2.31 | 53.961
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.0213 | 1.87 | 22.5 | 0 | 2.21 | 22 | 1.8913 | 2.21 | 16.851
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | 0.00275 | 1.21 | 21.833 | 0 | 2.27 | 22.333 | 1.2072 | 2.27 | 88.031
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.000891 | 1.35 | 21.833 | 0 | 1.47 | 21.833 | 1.3491 | 1.47 | 8.9608
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.00202 | 0.81783 | 22.333 | 0 | 1.33 | 21.833 | 0.81985 | 1.33 | 62.224
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | 0.00029 | 1.4667 | 19.833 | 0 | 1.48 | 22.167 | 1.4664 | 1.48 | 0.92903
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | -0.00807 | 1.3667 | 22.333 | 0 | 1.92 | 22.167 | 1.3747 | 1.92 | 39.663
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 365 | 0 | 30 | Max |  |  | 0.000461 | 1.8783 | 21.833 | 0 | 1.9 | 22 | 1.8779 | 1.9 | 1.1783
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | -0.0152 | 1.21 | 23.5 | 0 | 1.92 | 22.333 | 1.2252 | 1.92 | 56.709
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | -0.005 | 1.78 | 22.667 | 0 | 1.92 | 22.333 | 1.785 | 1.92 | 7.563
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | -0.0188 | 0.883 | 22.667 | 0 | 1.64 | 22.167 | 0.9018 | 1.64 | 81.859
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | 0.00255 | 2.32 | 10.5 | 0 | 1.6 | 22.167 | 2.3174 | 1.6 | -30.959
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | -0.00519 | 1.9367 | 22.333 | 0 | 2.15 | 22.167 | 1.9419 | 2.15 | 10.719
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372
Experiment | ICFMP3_Test_8 | 1
Model | ICFMP3_Test_8 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 28.8 | 247 | 10 | 25 | 259 | 10.167 | 218.2 | 234 | 7.2411
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.81 | 11.833 | 3.82 | 0.011433 | 10.167 | -3.01 | -3.8086
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 30.7 | 277.94 | 9.6667 | 25 | 259 | 10.167 | 247.24 | 234 | -5.3556
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.11317 | 10.667 | 0.203 | 0.105 | 10.167 | -0.095833 | -0.098 | 2.2609
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.057817 | 10.667 | 0 | 0.0574 | 10.333 | 0.057817 | 0.0574 | -0.72067
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 99.5 | 8 | 0 | 411 | 20.333 | 99.5 | 411 | 313.07
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 189 | 1.8333 | 0 | 214 | 3 | 189 | 214 | 13.227
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 28.9 | 212 | 10 | 25 | 167 | 10.167 | 183.1 | 142 | -22.447
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 29.4 | 179 | 10 | 25 | 168 | 10.167 | 149.6 | 143 | -4.4118
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 28.7 | 160 | 10 | 25 | 136 | 10.167 | 131.3 | 111 | -15.461
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 28.6 | 135 | 10.333 | 25 | 161 | 10.167 | 106.4 | 136 | 27.82
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 23.9 | 119 | 10.5 | 25 | 174 | 10.167 | 95.1 | 149 | 56.677
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 24.8 | 156.67 | 10.333 | 25 | 175 | 10.167 | 131.87 | 150 | 13.751
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 22.4 | 131 | 10.5 | 25 | 173 | 10.167 | 108.6 | 148 | 36.28
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 23 | 147.67 | 10.167 | 25 | 174 | 10.167 | 124.67 | 149 | 19.519
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 22.7 | 93.9 | 10.5 | 25 | 150 | 10.167 | 71.2 | 125 | 75.562
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 354 | 0 | 30 | Max |  |  | 24.8 | 173 | 10 | 25 | 146 | 10.167 | 148.2 | 121 | -18.354
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 27.6 | 174.83 | 10.167 | 25 | 177.67 | 10.167 | 147.23 | 152.67 | 3.6903
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 31.9 | 357 | 10 | 25 | 175.67 | 10.167 | 325.1 | 150.67 | -53.655
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.0411 | 5.54 | 10 | 0 | 5.73 | 10.167 | 5.5811 | 5.73 | 2.6679
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.0992 | 8.3757 | 9.1667 | 0 | 5.87 | 10.167 | 8.4749 | 5.87 | -30.736
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.00361 | 4.9106 | 8.8333 | 0 | 5.46 | 10.167 | 4.907 | 5.46 | 11.27
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.000627 | 5.9792 | 6.3333 | 0 | 5.44 | 10.167 | 5.9798 | 5.44 | -9.0277
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | 0.0039 | 2.919 | 9.8333 | 0 | 5.33 | 10.167 | 2.9151 | 5.33 | 82.84
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.00256 | 3.5588 | 9.8333 | 0 | 4.07 | 10.167 | 3.5563 | 4.07 | 14.446
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | 0.000246 | 1.9296 | 9.8333 | 0 | 3.66 | 10.167 | 1.9294 | 3.66 | 89.7
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.000435 | 6.0167 | 4.8333 | 0 | 4.08 | 10.167 | 6.0171 | 4.08 | -32.193
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.0488 | 3.89 | 10 | 0 | 4.61 | 10.167 | 3.8412 | 4.61 | 20.015
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.0557 | 3.2667 | 10.333 | 0 | 4.57 | 10.167 | 3.211 | 4.57 | 42.325
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | 0 | 30 | Max |  |  | -0.194 | 2.27 | 9.5 | 0 | 4.6067 | 10.167 | 2.464 | 4.6067 | 86.959
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.0462 | 4.7482 | 9.6667 | 0 | 4.6 | 10.167 | 4.702 | 4.6 | -2.17
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.0359 | 2.59 | 10 | 0 | 4.12 | 10.167 | 2.5541 | 4.12 | 61.309
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | 0.0692 | 8.7 | 6 | 0 | 4.01 | 10.167 | 8.6308 | 4.01 | -53.538
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.0882 | 6.2182 | 9.6667 | 0 | 5.0467 | 10.167 | 6.13 | 5.0467 | -17.673
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max |  |  | 0.142 | 13.1 | 10 | 0 | 4.9367 | 10.167 | 12.958 | 4.9367 | -61.903
Experiment | ICFMP3_Test_9 | 1
Model | ICFMP3_Test_9 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 28.7 | 232.83 | 23.167 | 27 | 268 | 23 | 204.13 | 241 | 18.06
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 | 0.9 | 22.5 | 3.82 | 1.02 | 3.5 | -2.92 | -2.8 | -4.1096
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 27.4 | 261.5 | 23.167 | 27 | 268 | 23 | 234.1 | 241 | 2.9476
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.15517 | 22.833 | 0.203 | 0.161 | 9 | -0.053833 | -0.042 | -21.982
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.0313 | 13 | 0 | 0.0269 | 11.833 | 0.0313 | 0.0269 | -14.058
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 116 | 14.5 | 0 | 139 | 9.8333 | 116 | 139 | 19.828
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 | -1.9467 | 24.667 | 0 | -2.1 | 23.5 | -1.9467 | -2.1 | 7.8772
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 27.5 | 255 | 23.667 | 27 | 245 | 23.167 | 227.5 | 218 | -4.1758
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 28.6 | 249 | 24.167 | 27 | 246 | 23 | 220.4 | 219 | -0.63521
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 27.4 | 222 | 23.667 | 27 | 183 | 22.833 | 194.6 | 156 | -19.836
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 27.6 | 194 | 23.833 | 27 | 248 | 23.167 | 166.4 | 221 | 32.812
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 23.1 | 136 | 23.667 | 27 | 211 | 23.167 | 112.9 | 184 | 62.976
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 24.1 | 201.83 | 23.333 | 27 | 227 | 23 | 177.73 | 200 | 12.528
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max |  |  | 21.9 | 109.83 | 23.833 | 27 | 175 | 23 | 87.933 | 148 | 68.309
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 139 | 325 | 346 | 0 | 30 | Max |  |  | 22.1 | 156.83 | 23.833 | 27 | 215 | 23.167 | 134.73 | 188 | 39.535
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 21.9 | 74.983 | 23.833 | 27 | 166 | 23.167 | 53.083 | 139 | 161.85
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 23.2 | 145 | 22.333 | 27 | 162 | 23.333 | 121.8 | 135 | 10.837
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 166 | 325 | 348 | 0 | 30 | Max |  |  | 27.4 | 231 | 21.833 | 27 | 218 | 23.167 | 203.6 | 191 | -6.1886
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 38.1 | 328 | 22 | 27 | 221 | 22.833 | 289.9 | 194 | -33.08
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.0343 | 6.5433 | 21.167 | 0 | 6.3 | 23 | 6.5776 | 6.3 | -4.2208
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.0279 | 9.03 | 23 | 0 | 6.46 | 23 | 9.0579 | 6.46 | -28.681
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.02 | 5.06 | 20.5 | 0 | 5.97 | 22.833 | 5.08 | 5.97 | 17.52
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.0423 | 6.3083 | 22.667 | 0 | 6.41 | 23 | 6.3506 | 6.41 | 0.93499
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.0237 | 4.2617 | 22.833 | 0 | 5.47 | 23 | 4.2854 | 5.47 | 27.644
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | -0.0281 | 5.2167 | 22.833 | 0 | 4.62 | 22.833 | 5.2448 | 4.62 | -11.912
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.0115 | 2.72 | 22.833 | 0 | 4.13 | 22.833 | 2.7315 | 4.13 | 51.199
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.0547 | 5.0992 | 3.6667 | 0 | 5.02 | 23 | 5.1539 | 5.02 | -2.5983
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.0433 | 3.46 | 23 | 0 | 4.68 | 23 | 3.4167 | 4.68 | 36.974
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.0678 | 4.27 | 23.167 | 0 | 5.17 | 22.833 | 4.2022 | 5.17 | 23.031
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | 0.0337 | 2.425 | 23.667 | 0 | 3.34 | 23 | 2.3913 | 3.34 | 39.674
Compare | Short Wall 2 Flux | Surface Flux | 1 | 17 | 325 | 369 | [14 empty] | No experimental measureme
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.0257 | 1.9383 | 23.333 | 0 | 3.43 | 23 | 1.9126 | 3.43 | 79.334
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max |  |  | 0.066 | 3.9267 | 22.667 | 0 | 3.31 | 23 | 3.8607 | 3.31 | -14.263
Compare | Ceiling 1 Flux | Surface Flux | 1 | 31 | 325 | 371 | 0 | 30 | Max |  |  | 0.137 | 5.59 | 22 | 0 | 5.27 | 23 | 5.453 | 5.27 | -3.3559
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | 0 | 30 | Max |  |  | 0.297 | 9.7 | 22 | 0 | 5.39 | 23 | 9.403 | 5.39 | -42.678
Experiment | ICFMP3_Test_10 | 1
Model | ICFMP3_Test_10 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 23.7 | 222 | 13.5 | 27 | 248 | 13.667 | 198.3 | 221 | 11.447
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.595 | 17.333 | 3.82 | 0.018733 | 13.667 | -3.225 | -3.8013
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 22.5 | 239.5 | 13.333 | 27 | 248 | 13.667 | 217 | 221 | 1.8434
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.13017 | 14.167 | 0.203 | 0.143 | 13.5 | -0.078833 | -0.06 | -23.89
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.046433 | 14.167 | 0 | 0.0347 | 13.667 | 0.046433 | 0.0347 | -25.269
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 70.684 | 7.3333 | 0 | 177 | 13.833 | 70.684 | 177 | 150.41
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 49.267 | 1.8333 | 0 | 45.7 | 3 | 49.267 | 45.7 | -7.2395
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 26.5 | 170 | 13 | 27 | 188.67 | 13.667 | 143.5 | 161.67 | 12.66
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 26.8 | 158.67 | 13.167 | 27 | 190 | 13.667 | 131.87 | 163 | 23.61
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 26 | 176 | 13.833 | 27 | 155 | 13.5 | 150 | 128 | -14.667
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 26.7 | 174.67 | 13.833 | 27 | 176 | 13.667 | 147.97 | 149 | 0.6984
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 21.9 | 116 | 13.833 | 27 | 177 | 13.833 | 94.1 | 150 | 59.405
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 22.8 | 184.5 | 13.667 | 27 | 178 | 13.5 | 161.7 | 151 | -6.6173
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max |  |  | 21 | 127 | 14 | 27 | 176 | 13.667 | 106 | 149 | 40.566
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 21.1 | 138 | 13.5 | 27 | 177 | 13.833 | 116.9 | 150 | 28.315
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 21.5 | 92.6 | 14 | 27 | 156.67 | 13.667 | 71.1 | 129.67 | 82.372
Compare | Floor 2 Temperature | Surface Temperature | 1 | 155 | 325 | 353 | 0 | 30 | Max |  |  | 22.3 | 178.17 | 13.833 | 27 | 153.67 | 13.667 | 155.87 | 126.67 | -18.734
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 24.8 | 162.67 | 13.833 | 27 | 180 | 13.667 | 137.87 | 153 | 10.977
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 24.8 | 245.96 | 3.3333 | 27 | 179 | 13.5 | 221.16 | 152 | -31.272
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.00396 | 4.8317 | 13.667 | 0 | 5.33 | 13.667 | 4.8356 | 5.33 | 10.223
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | 0.0499 | 6.7 | 12 | 0 | 5.46 | 13.667 | 6.6501 | 5.46 | -17.896
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.0616 | 4.2583 | 13.333 | 0 | 5.09 | 13.667 | 4.3199 | 5.09 | 17.826
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | 0.149 | 6.35 | 13.5 | 0 | 5.03 | 13.667 | 6.201 | 5.03 | -18.884
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.0119 | 2.6633 | 13.667 | 0 | 4.9267 | 13.667 | 2.6752 | 4.9267 | 84.158
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | -0.00635 | 2.91 | 12 | 0 | 3.77 | 13.667 | 2.9163 | 3.77 | 29.271
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.00419 | 1.915 | 13.667 | 0 | 3.4 | 13.667 | 1.9192 | 3.4 | 77.158
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.00502 | 5.418 | 6.1667 | 0 | 3.76 | 13.667 | 5.4231 | 3.76 | -30.666
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.0281 | 3.3667 | 13.667 | 0 | 4.23 | 13.667 | 3.3386 | 4.23 | 26.701
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.0334 | 3.5133 | 13.667 | 0 | 4.23 | 13.667 | 3.4799 | 4.23 | 21.554
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | 0.0219 | 3.1267 | 13.667 | 0 | 4.2267 | 13.667 | 3.1048 | 4.2267 | 36.135
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.0267 | 3.9017 | 13.667 | 0 | 4.22 | 13.667 | 3.875 | 4.22 | 8.9041
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.0188 | 2.29 | 13.5 | 0 | 3.85 | 13.667 | 2.2712 | 3.85 | 69.514
Compare | Floor 2 Flux | Surface Flux | 1 | 25 | 325 | 377 | 0 | 30 | Max |  |  | 0.117 | 8.01 | 6.5 | 0 | 3.77 | 13.667 | 7.893 | 3.77 | -52.236
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.0263 | 4.745 | 13.833 | 0 | 4.63 | 13.667 | 4.7187 | 4.63 | -1.8794
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372
Experiment | ICFMP3_Test_13 | 1
Model | ICFMP3_Test_13 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 32.6 | 322.84 | 5.8333 | 31 | 342 | 6 | 290.24 | 311 | 7.1515
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.84 | 7.6667 | 3.82 | 0.0169 | 6 | -2.98 | -3.8031
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 33.5 | 363.55 | 5.8333 | 31 | 342 | 6 | 330.05 | 311 | -5.7716
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.1082 | 6.1667 | 0.202 | 0.0923 | 6.1667 | -0.1008 | -0.1097 | 8.8252
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.059988 | 6.1667 | 0 | 0.0644 | 6.1667 | 0.059988 | 0.0644 | 7.3545
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 223.73 | 5.1667 | 0 | 480 | 27.833 | 223.73 | 480 | 114.55
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 232 | 2 | 0 | 336 | 2.8333 | 232 | 336 | 44.828
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 33.5 | 218.96 | 6.1667 | 31 | 196 | 6 | 185.46 | 165 | -11.032
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 34.5 | 208 | 4.5 | 31 | 199 | 6 | 173.5 | 168 | -3.17
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 33.6 | 176.98 | 5.6667 | 31 | 174 | 6 | 143.38 | 143 | -0.26536
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 34.1 | 167 | 6 | 31 | 195 | 6 | 132.9 | 164 | 23.401
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 28.6 | 138.98 | 6.1667 | 31 | 226 | 6 | 110.38 | 195 | 76.662
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 29.8 | 229 | 6 | 31 | 229 | 6 | 199.2 | 198 | -0.60243
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 27.2 | 154 | 6.1667 | 31 | 225 | 6 | 126.8 | 194 | 52.997
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 139 | 325 | 346 | 0 | 30 | Max |  |  | 27.4 | 172 | 6 | 31 | 226 | 6 | 144.6 | 195 | 34.855
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 27.4 | 116.98 | 6.1667 | 31 | 197 | 6 | 89.58 | 166 | 85.308
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 28.7 | 177 | 4.8333 | 31 | 192 | 6 | 148.3 | 161 | 8.5637
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 177 | 325 | 351 | 0 | 30 | Max |  |  | 33.7 | 352.73 | 5.8333 | 31 | 227 | 6 | 319.03 | 196 | -38.563
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max |  |  | 35.4 | 532.84 | 5.6667 | 31 | 228 | 6 | 497.44 | 197 | -60.397
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.0104 | 8.2402 | 5.6667 | 0 | 9.67 | 6 | 8.2506 | 9.67 | 17.204
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | 0.0338 | 11.292 | 4.3333 | 0 | 9.95 | 6 | 11.258 | 9.95 | -11.621
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.0436 | 7.3169 | 5.6667 | 0 | 9.15 | 6 | 7.2733 | 9.15 | 25.803
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.0336 | 12.052 | 5.8333 | 0 | 9.38 | 6 | 12.086 | 9.38 | -22.387
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | 0.00149 | 4.769 | 4.6667 | 0 | 8.88 | 6 | 4.7675 | 8.88 | 86.26
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.00468 | 6.579 | 4.3333 | 0 | 7.58 | 6 | 6.5743 | 7.58 | 15.297
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.00182 | 2.8988 | 4.6667 | 0 | 6.79 | 6 | 2.9006 | 6.79 | 134.09
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.000145 | 10.1 | 3.5 | 0 | 7.6 | 6 | 10.1 | 7.6 | -24.754
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | [14 empty] | No experimental measureme
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | [14 empty] | No experimental measureme
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | [14 empty] | No experimental measureme
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 369 | [14 empty] | No experimental measureme
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | [14 empty] | No experimental measureme
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | [14 empty] | No experimental measureme
Compare | Ceiling 1 Flux | Surface Flux | 1 | 36 | 325 | 374 | [14 empty] | No experimental measureme
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | [14 empty] | No experimental measureme
Experiment | ICFMP3_Test_14 | 1
Model | ICFMP3_Test_14 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 26.3 | 234 | 22.833 | 28 | 270 | 23.167 | 207.7 | 242 | 16.514
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 | 0.91 | 22.5 | 3.82 | 1.01 | 3.6667 | -2.91 | -2.81 | -3.4364
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 26.2 | 267 | 22 | 28 | 270 | 23.167 | 240.8 | 242 | 0.49848
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.154 | 12.833 | 0.202 | 0.16 | 11.333 | -0.055 | -0.042 | -23.636
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.0322 | 14.5 | 0 | 0.0271 | 12.333 | 0.0322 | 0.0271 | -15.838
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 91.3 | 27 | 0 | 139 | 9.3333 | 91.3 | 139 | 52.246
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 | -2.0367 | 25.333 | 0 | -2.12 | 23.667 | -2.0367 | -2.12 | 4.0912
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 28 | 227 | 23.333 | 28 | 235 | 23.667 | 199 | 207 | 4.0201
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 28.7 | 207 | 23.333 | 28 | 236 | 23.5 | 178.3 | 208 | 16.657
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 27.8 | 199 | 23.833 | 28 | 173 | 23.333 | 171.2 | 145 | -15.304
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 28.1 | 298 | 21.333 | 28 | 290 | 23 | 269.9 | 262 | -2.927
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 23.6 | 138 | 23.833 | 28 | 212 | 23.167 | 114.4 | 184 | 60.839
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 24.3 | 278.67 | 23.167 | 28 | 250 | 23 | 254.37 | 222 | -12.724
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 343 | 0 | 30 | Max |  |  | 22.2 | 109 | 24 | 28 | 177 | 23.167 | 86.8 | 149 | 71.659
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 22.4 | 170 | 23.667 | 28 | 217 | 23.167 | 147.6 | 189 | 28.049
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 22.5 | 74.7 | 24.167 | 28 | 169 | 23.333 | 52.2 | 141 | 170.11
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 23.2 | 127 | 23.667 | 28 | 165 | 23.5 | 103.8 | 137 | 31.985
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 26.3 | 184 | 23.667 | 28 | 220 | 23.167 | 157.7 | 192 | 21.75
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max |  |  | 29.2 | 379.83 | 22.667 | 28 | 228 | 23 | 350.63 | 200 | -42.96
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | 0.0107 | 3.83 | 22 | 0 | 5.78 | 23 | 3.8193 | 5.78 | 51.337
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.0132 | 6.04 | 24 | 0 | 5.94 | 23 | 6.0532 | 5.94 | -1.8696
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.00639 | 3.45 | 22.167 | 0 | 5.52 | 23 | 3.4436 | 5.52 | 60.297
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.001 | 10.833 | 22.333 | 0 | 8.32 | 23 | 10.834 | 8.32 | -23.207
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | 0.000229 | 2.8333 | 23.167 | 0 | 5.54 | 23 | 2.8331 | 5.54 | 95.545
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.00234 | 3.3117 | 23.333 | 0 | 4.09 | 22.833 | 3.3093 | 4.09 | 23.59 | No experimental measureme
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | 0.00118 | 2.1167 | 23.333 | 0 | 3.68 | 23 | 2.1155 | 3.68 | 73.955
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.00135 | 10.5 | 2.5 | 0 | 6.92 | 23 | 10.501 | 6.92 | -34.104
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.0416 | 3.5317 | 23.167 | 0 | 4.7 | 23 | 3.4901 | 4.7 | 34.668
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.05 | 8.15 | 23 | 0 | 5.9 | 23 | 8.1 | 5.9 | -27.16
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | 0.0329 | 2.375 | 22.833 | 0 | 3.4 | 22.833 | 2.3421 | 3.4 | 45.169
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.0412 | 4.51 | 23 | 0 | 4.84 | 23 | 4.4688 | 4.84 | 8.3066
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.0301 | 1.92 | 23.333 | 0 | 3.49 | 23 | 1.8899 | 3.49 | 84.666
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max |  |  | 0.0389 | 3.01 | 23 | 0 | 3.37 | 23 | 2.9711 | 3.37 | 13.426
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.047 | 4.73 | 23.333 | 0 | 5.33 | 23 | 4.683 | 5.33 | 13.816
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | 0 | 30 | Max |  |  | 0.0944 | 9.09 | 19.5 | 0 | 5.6 | 23 | 8.9956 | 5.6 | -37.747
Experiment | ICFMP3_Test_15 | 1
Model | ICFMP3_Test_15 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 22.8 | 233 | 22.833 | 18 | 260 | 22.833 | 210.2 | 242 | 15.128
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 | 0.93 | 23 | 3.82 | 1.03 | 3.5 | -2.89 | -2.79 | -3.4602
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 22.2 | 266 | 23 | 18 | 260 | 22.833 | 243.8 | 242 | -0.73828
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.158 | 12.5 | 0.203 | 0.161 | 10.333 | -0.051 | -0.042 | -17.647
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.0312 | 15.833 | 0 | 0.0267 | 12.667 | 0.0312 | 0.0267 | -14.423
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 124 | 30 | 0 | 140 | 10.833 | 124 | 140 | 12.904
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 | -2.325 | 25.667 | 0 | -2.2 | 23.667 | -2.325 | -2.2 | -5.3755
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 31.9 | 447 | 9.5 | 18 | 225 | 23.333 | 415.1 | 207 | -50.132
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 25.9 | 269 | 27.333 | 18 | 227 | 23.333 | 243.1 | 209 | -14.027
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 25.1 | 695 | 23.5 | 18 | 173 | 23.167 | 669.9 | 155 | -76.862
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 25.5 | 186.83 | 24.333 | 18 | 281 | 22.833 | 161.33 | 263 | 63.016
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 125 | 325 | 340 | 0 | 30 | Max |  |  | 22.8 | 242 | 22.667 | 18 | 201 | 23.167 | 219.2 | 183 | -16.515
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 124 | 325 | 341 | 0 | 30 | Max |  |  | 22.8 | 228 | 23 | 18 | 206 | 23.333 | 205.2 | 188 | -8.382
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 343 | 0 | 30 | Max |  |  | 19.2 | 115 | 23.5 | 18 | 163 | 23.167 | 95.8 | 145 | 51.357
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 19 | 170 | 23.333 | 18 | 205 | 23.167 | 151 | 187 | 23.841
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 19.9 | 72.133 | 24.167 | 18 | 155 | 23.5 | 52.233 | 137 | 162.28
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 21.9 | 153 | 24.5 | 18 | 150 | 23.167 | 131.1 | 132 | 0.68666
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 24 | 181 | 23.333 | 18 | 209 | 23.333 | 157 | 191 | 21.656
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 25.9 | 313 | 23 | 18 | 204 | 23.167 | 287.1 | 186 | -35.214
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.558 | 57.2 | 2.5 | 0 | 5.58 | 23 | 57.758 | 5.58 | -90.339
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | 0.00731 | 20.9 | 4 | 0 | 5.74 | 23 | 20.893 | 5.74 | -72.526
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.44 | 23.5 | 20.5 | 0 | 5.33 | 23 | 23.94 | 5.33 | -77.736
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.039 | 5.0383 | 22.167 | 0 | 8.14 | 23 | 5.0773 | 8.14 | 60.321
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.607 | 45.788 | 3.1667 | 0 | 5.3333 | 23.167 | 46.395 | 5.3333 | -88.505
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | [14 empty] | No experimental measureme
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.265 | 17.9 | 20.5 | 0 | 3.43 | 23 | 18.165 | 3.43 | -81.117
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.0853 | 3.65 | 23 | 0 | 6.7 | 22.833 | 3.7353 | 6.7 | 79.37
Compare | Long Wall 1 Flux | Surface Flux | 1 | 8 | 325 | 363 | 0 | 30 | Max |  |  | 0.0238 | 3.66 | 23 | 0 | 4.54 | 23 | 3.6362 | 4.54 | 24.856
Compare | Long Wall 2 Flux | Surface Flux | 1 | 10 | 325 | 364 | 0 | 30 | Max |  |  | 0.147 | 7.5996 | 3.3333 | 0 | 4.67 | 23 | 7.4526 | 4.67 | -37.337
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | 0.0122 | 2.595 | 21.833 | 0 | 3.2 | 22.833 | 2.5828 | 3.2 | 23.896
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.0206 | 4.6717 | 22.667 | 0 | 4.66 | 23.167 | 4.6511 | 4.66 | 0.19215
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | -0.00446 | 1.9383 | 23.167 | 0 | 3.26 | 23 | 1.9428 | 3.26 | 67.8
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max |  |  | 0.0536 | 5.225 | 23.333 | 0 | 3.15 | 23.167 | 5.1714 | 3.15 | -39.088
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372
Experiment | ICFMP3_Test_16 | 1
Model | ICFMP3_Test_16 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 21.4 | 289.86 | 6.3333 | 26 | 316 | 6.3333 | 268.46 | 290 | 8.0224
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.53 | 23.833 | 3.82 | 0.015783 | 6.3333 | -3.29 | -3.8042
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 20.7 | 298 | 6.3333 | 26 | 316 | 6.3333 | 277.3 | 290 | 4.5799
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.11806 | 6.8333 | 0.203 | 0.128 | 6.3333 | -0.090941 | -0.075 | -17.529
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.05518 | 6.8333 | 0 | 0.043817 | 6.3333 | 0.05518 | 0.043817 | -20.594
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 139 | 4.5 | 0 | 205 | 6.8333 | 139 | 205 | 47.482
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 80.529 | 1.6667 | 0 | 225 | 2.8333 | 80.529 | 225 | 179.4
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 23.9 | 184 | 6.6667 | 26 | 192 | 6.3333 | 160.1 | 166 | 3.6852
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 23.4 | 178.51 | 5.6667 | 26 | 196 | 6.3333 | 155.11 | 170 | 9.5999
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 23.8 | 192 | 6.6667 | 26 | 174 | 6.3333 | 168.2 | 148 | -12.01
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 24.5 | 193.96 | 6.1667 | 26 | 176.17 | 6.3333 | 169.46 | 150.17 | -11.386
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 19.7 | 127 | 6.5 | 26 | 201.17 | 6.3333 | 107.3 | 175.17 | 63.249
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 20.9 | 237.96 | 6.1667 | 26 | 206.17 | 6.3333 | 217.06 | 180.17 | -16.997
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 133 | 325 | 343 | 0 | 30 | Max |  |  | 19 | 142 | 6.3333 | 26 | 201 | 6.3333 | 123 | 175 | 42.276
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 18.9 | 160 | 6.5 | 26 | 202 | 6.3333 | 141.1 | 176 | 24.734
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 20 | 99.992 | 6.6667 | 26 | 174.17 | 6.3333 | 79.992 | 148.17 | 85.226
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 20.5 | 166 | 6.3333 | 26 | 170 | 6.3333 | 145.5 | 144 | -1.0309
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 177 | 325 | 351 | 0 | 30 | Max |  |  | 22.8 | 306 | 6.5 | 26 | 204 | 6.3333 | 283.2 | 178 | -37.147
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 173 | 325 | 350 | 0 | 30 | Max |  |  | 23.4 | 464.84 | 6.3333 | 26 | 206 | 6.3333 | 441.44 | 180 | -59.225
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.323 | 8.0237 | 6.1667 | 0 | 8.4517 | 6.3333 | 8.3467 | 8.4517 | 1.2574
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.415 | 11.271 | 6.1667 | 0 | 8.7017 | 6.3333 | 11.686 | 8.7017 | -25.537
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.079 | 6.06 | 5.5 | 0 | 7.9717 | 6.3333 | 6.139 | 7.9717 | 29.853
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.0146 | 12.163 | 5.3333 | 0 | 8.1417 | 6.3333 | 12.177 | 8.1417 | -33.141
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.0662 | 4.0416 | 6.1667 | 0 | 7.6717 | 6.3333 | 4.1078 | 7.6717 | 86.76
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | -0.0932 | 4.73 | 5.5 | 0 | 6.4717 | 6.3333 | 4.8232 | 6.4717 | 34.178
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.0293 | 2.7276 | 6.3333 | 0 | 5.7417 | 6.3333 | 2.7569 | 5.7417 | 108.26
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.175 | 11.8 | 4 | 0 | 6.4517 | 6.3333 | 11.975 | 6.4517 | -46.124
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | [14 empty] | No experimental measureme
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | [14 empty] | No experimental measureme
Compare | Short Wall 1 Flux | Surface Flux | 1 | 14 | 325 | 366 | [14 empty] | No experimental measureme
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | [14 empty] | No experimental measureme
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | [14 empty] | No experimental measureme
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | [14 empty] | No experimental measureme
Compare | Ceiling 1 Flux | Surface Flux | 1 | 36 | 325 | 374 | [14 empty] | No experimental measureme
Compare | Ceiling 2 Flux | Surface Flux | 1 | 34 | 325 | 373 | [14 empty] | No experimental measureme
Experiment | ICFMP3_Test_17 | 1
Model | ICFMP3_Test_17 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 25.7 | 161 | 4.5 | 27 | 170 | 4.5 | 135.3 | 143 | 5.6911
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min | Closed |  | 3.82 | 0.6902 | 5.8333 | 3.82 | 0.49 | 4.5 | -3.1298 | -3.33
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 24.6 | 180 | 4.3333 | 27 | 170 | 4.5 | 155.4 | 143 | -7.9794
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.17604 | 4.8333 | 0.204 | 0.173 | 4.6667 | -0.032961 | -0.031 | -5.9488
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.021576 | 4.8333 | 0 | 0.0166 | 4.6667 | 0.021576 | 0.0166 | -23.064
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 352.84 | 4.6667 | 0 | 1590 | 14.333 | 352.84 | 1590 | 350.63
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Max |  |  | 0 | 194.82 | 3.3333 | 0 | 137 | 3 | 194.82 | 137 | -29.68
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | [14 empty] | No experimental measureme
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | [14 empty] | No experimental measureme
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | [14 empty] | No experimental measureme
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | [14 empty] | No experimental measureme
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 109 | 325 | 338 | 0 | 30 | Max |  |  | 23.6 | 62.6 | 4.8333 | 27 | 79.9 | 4.6667 | 39 | 52.9 | 35.641
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 115 | 325 | 339 | 0 | 30 | Max |  |  | 24 | 106 | 4.5 | 27 | 92.2 | 4.5 | 82 | 65.2 | -20.488
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 345 | 0 | 30 | Max |  |  | 22.1 | 78.463 | 4.6667 | 27 | 78.6 | 4.6667 | 56.363 | 51.6 | -8.4502
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 22.4 | 83.365 | 4.6667 | 27 | 81.017 | 4.6667 | 60.965 | 54.017 | -11.397
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 22.1 | 46.5 | 5 | 27 | 61.1 | 4.6667 | 24.4 | 34.1 | 39.754
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 22.1 | 74 | 4.5 | 27 | 59.5 | 4.6667 | 51.9 | 32.5 | -37.38
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 26.4 | 95.073 | 4.6667 | 27 | 84.717 | 4.6667 | 68.673 | 57.717 | -15.954
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 27.1 | 256.86 | 4.1667 | 27 | 91.3 | 4.5 | 229.76 | 64.3 | -72.015
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.021 | 2.3394 | 4.3333 | 0 | 3.03 | 4.5 | 2.3604 | 3.03 | 28.367
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.125 | 3.1533 | 4.3333 | 0 | 3.14 | 4.5 | 3.2783 | 3.14 | -4.2196
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | 0.00442 | 1.8584 | 4.6667 | 0 | 2.82 | 4.5 | 1.854 | 2.82 | 52.103
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | -0.00439 | 3.0563 | 4.1667 | 0 | 2.94 | 4.5 | 3.0607 | 2.94 | -3.9424
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | -0.00161 | 1.2994 | 4.3333 | 0 | 2.5 | 4.5 | 1.301 | 2.5 | 92.157
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | 0 | 30 | Max |  |  | 0.0107 | 1.5296 | 4.1667 | 0 | 2.09 | 4.5 | 1.5189 | 2.09 | 37.599
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | 0.000246 | 0.882 | 4.5 | 0 | 1.76 | 4.5 | 0.88175 | 1.76 | 99.602
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | 0.00135 | 2.4175 | 2.6667 | 0 | 2.18 | 3 | 2.4161 | 2.18 | -9.772
Compare | Long Wall 1 Flux | Surface Flux | 1 | 2 | 325 | 361 | 0 | 30 | Max |  |  | 0.00329 | 1.47 | 4.5 | 0 | 2.16 | 4.5 | 1.4667 | 2.16 | 47.268
Compare | Long Wall 2 Flux | Surface Flux | 1 | 5 | 325 | 362 | 0 | 30 | Max |  |  | 0.0014 | 0.93 | 4.5 | 0 | 2.36 | 4.5 | 0.9286 | 2.36 | 154.15
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | 0.00668 | 1.5696 | 4.3333 | 0 | 2.15 | 4.5 | 1.5629 | 2.15 | 37.562
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.01 | 1.9088 | 4.3333 | 0 | 2.16 | 4.5 | 1.8988 | 2.16 | 13.755
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.00831 | 0.865 | 4.5 | 0 | 1.4 | 4.5 | 0.85669 | 1.4 | 63.42
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max |  |  | 0.0119 | 1.5096 | 4.1667 | 0 | 1.35 | 4.5 | 1.4977 | 1.35 | -9.8623
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | [14 empty] | No experimental measureme
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | [14 empty] | No experimental measureme
Experiment | ICFMP3_Test_18 | 1
Model | ICFMP3_Test_18 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 1 | 254 | 325 | 326 | 0 | 30 | Max |  |  | 24.5 | 217.83 | 23.167 | 27 | 270 | 23 | 193.33 | 243 | 25.69
Compare | HGL Height | HGL Height | 1 | 252 | 325 | 327 | 0 | 30 | Min |  |  | 3.82 | 0.91 | 16.5 | 3.82 | 1.01 | 3.6667 | -2.91 | -2.81 | -3.4364
Compare | Tree 7 3.50 m height | Ceiling Jet Temperature | 1 | 107 | 325 | 326 | 0 | 30 | Max |  |  | 24.3 | 259 | 22.5 | 27 | 270 | 23 | 234.7 | 243 | 3.5366
Compare | Oxygen | Oxygen | 1 | 220 | 325 | 329 | 0 | 25 | Min |  |  | 0.209 | 0.159 | 13.833 | 0.204 | 0.16 | 11.667 | -0.05 | -0.044 | -12
Compare | Carbon Dioxide | Carbon Dioxide | 1 | 223 | 325 | 330 | 0 | 25 | Max |  |  | 0 | 0.0306 | 22.833 | 0 | 0.0272 | 12.5 | 0.0306 | 0.0272 | -11.111
Compare | Smoke Concentration | Smoke Concentration | 1 | 224 | 325 | 331 | 0 | 30 | Max |  |  | 0 | 109.5 | 19.833 | 0 | 140 | 10 | 109.5 | 140 | 27.854
Compare | Pressure | Pressure | 1 | 235 | 325 | 328 | 0 | 30 | Min |  |  | 0 | -2.01 | 26 | 0 | -2.15 | 23.667 | -2.01 | -2.15 | 6.9658
Compare | Cable B Temperature | Cable Temperature | 1 | 192 | 325 | 332 | 0 | 30 | Max |  |  | 26.5 | 262 | 23.333 | 27 | 254 | 23.167 | 235.5 | 227 | -3.6093
Compare | Cable D Temperature | Cable Temperature | 1 | 190 | 325 | 333 | 0 | 30 | Max |  |  | 26.8 | 244 | 23.5 | 27 | 249 | 23.5 | 217.2 | 222 | 2.21
Compare | Cable F Temperature | Cable Temperature | 1 | 199 | 325 | 335 | 0 | 30 | Max |  |  | 26.1 | 257.83 | 23.167 | 27 | 215 | 22.833 | 231.73 | 188 | -18.872
Compare | G33 Temperature | Cable Temperature | 1 | 211 | 325 | 337 | 0 | 30 | Max |  |  | 25.5 | 135 | 25.167 | 27 | 230 | 23.333 | 109.5 | 203 | 85.388 | No experimental measureme
Compare | Long Wall 1 Temperature | Surface Temperature | 1 | 121 | 325 | 338 | 0 | 30 | Max |  |  | 22.9 | 141 | 23.833 | 27 | 212 | 23.333 | 118.1 | 185 | 56.647
Compare | Long Wall 2 Temperature | Surface Temperature | 1 | 127 | 325 | 342 | 0 | 30 | Max |  |  | 23.3 | 335.83 | 23.167 | 27 | 275 | 22.833 | 312.53 | 248 | -20.648
Compare | Short Wall 1 Temperature | Surface Temperature | 1 | 137 | 325 | 343 | 0 | 30 | Max |  |  | 20.2 | 114 | 23.333 | 27 | 181 | 23 | 93.8 | 154 | 64.179
Compare | Short Wall 2 Temperature | Surface Temperature | 1 | 135 | 325 | 344 | 0 | 30 | Max |  |  | 20.4 | 173 | 23.667 | 27 | 217 | 23.167 | 152.6 | 190 | 24.509
Compare | Floor 1 Temperature | Surface Temperature | 1 | 149 | 325 | 352 | 0 | 30 | Max |  |  | 20.9 | 70.433 | 24.667 | 27 | 168 | 23.167 | 49.533 | 141 | 184.66
Compare | Floor 2 Temperature | Surface Temperature | 1 | 151 | 325 | 353 | 0 | 30 | Max |  |  | 20.8 | 127 | 23.333 | 27 | 164 | 23.167 | 106.2 | 137 | 29.002
Compare | Ceiling 1 Temperature | Surface Temperature | 1 | 165 | 325 | 347 | 0 | 30 | Max |  |  | 25.4 | 170 | 23.333 | 27 | 220 | 23.167 | 144.6 | 193 | 33.472
Compare | Ceiling 2 Temperature | Surface Temperature | 1 | 171 | 325 | 349 | 0 | 30 | Max |  |  | 25.2 | 274.83 | 22.333 | 27 | 221 | 23.167 | 249.63 | 194 | -22.286
Compare | Cable B Flux | Cable Flux | 1 | 228 | 325 | 355 | 0 | 30 | Max |  |  | -0.000825 | 7.5717 | 23.167 | 0 | 6.71 | 23 | 7.5725 | 6.71 | -11.39
Compare | Cable D Flux | Cable Flux | 1 | 232 | 325 | 356 | 0 | 30 | Max |  |  | -0.0092 | 7.7966 | 23.167 | 0 | 6.56 | 23 | 7.8059 | 6.56 | -15.96
Compare | Cable F Flux | Cable Flux | 1 | 226 | 325 | 358 | 0 | 30 | Max |  |  | -0.00557 | 8.665 | 23.167 | 0 | 7.29 | 23 | 8.6705 | 7.29 | -15.922
Compare | G33 Flux | Cable Flux | 1 | 233 | 325 | 360 | 0 | 30 | Max |  |  | 0.00778 | 4.46 | 23.5 | 0 | 5.57 | 23 | 4.4522 | 5.57 | 25.106
Compare | Cable B Radiant Flux | Cable Radiant Flux | 1 | 227 | 325 | 378 | 0 | 30 | Max |  |  | 0.00321 | 5.21 | 22.167 | 0 | 5.57 | 23 | 5.2068 | 5.57 | 6.9759
Compare | Cable D Radiant Flux | Cable Radiant Flux | 1 | 231 | 325 | 379 | [14 empty] | No experimental measureme
Compare | Cable F Radiant Flux | Cable Radiant Flux | 1 | 225 | 325 | 381 | 0 | 30 | Max |  |  | -0.00227 | 5.14 | 22.167 | 0 | 5.43 | 23 | 5.1423 | 5.43 | 5.5957
Compare | G33 Radiant Flux | Cable Radiant Flux | 1 | 234 | 325 | 382 | 0 | 30 | Max |  |  | -0.00309 | 2.84 | 23.167 | 0 | 4.17 | 23 | 2.8431 | 4.17 | 46.671
Compare | Long Wall 1 Flux | Surface Flux | 1 | 8 | 325 | 363 | 0 | 30 | Max |  |  | 0.0301 | 3.43 | 23.5 | 0 | 4.68 | 23 | 3.3999 | 4.68 | 37.651
Compare | Long Wall 2 Flux | Surface Flux | 1 | 11 | 325 | 365 | [14 empty] | No experimental measureme
Compare | Short Wall 1 Flux | Surface Flux | 1 | 16 | 325 | 368 | 0 | 30 | Max |  |  | 0.0109 | 2.56 | 23.167 | 0 | 3.43 | 23 | 2.5491 | 3.43 | 34.558
Compare | Short Wall 2 Flux | Surface Flux | 1 | 15 | 325 | 367 | 0 | 30 | Max |  |  | 0.025 | 4.6817 | 22.333 | 0 | 4.88 | 23 | 4.6567 | 4.88 | 4.7959
Compare | Floor 1 Flux | Surface Flux | 1 | 22 | 325 | 375 | 0 | 30 | Max |  |  | 0.0175 | 1.8067 | 23.333 | 0 | 3.5 | 23 | 1.7892 | 3.5 | 95.622
Compare | Floor 2 Flux | Surface Flux | 1 | 23 | 325 | 376 | 0 | 30 | Max |  |  | 0.019 | 3.0767 | 23.167 | 0 | 3.38 | 23 | 3.0577 | 3.38 | 10.542
Compare | Ceiling 1 Flux | Surface Flux | 1 | 30 | 325 | 370 | 0 | 30 | Max |  |  | 0.0337 | 4.51 | 22.833 | 0 | 5.35 | 23 | 4.4763 | 5.35 | 19.518
Compare | Ceiling 2 Flux | Surface Flux | 1 | 33 | 325 | 372 | [14 empty] | No experimental measureme
Experiment | ICFMP4_Test_1 | 1
Model | ICFMP4_Test_1 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 117 | 136 | 1 | 2 | 0 | 30 | Max |  |  | 19.1 | 719.5 | 22.833 | 20 | 638 | 22.667 | 700.4 | 618 | -11.765
Compare | HGL Height | HGL Height | 117 | 138 | 1 | 3 | 0 | 20 | Min |  |  | 5.7 | 1.5 | 10.333 | 5.7 | 0.62 | 20 | -4.2 | -5.08 | 20.952
Compare | Steel Heat Flux | Surface Temperature | 117 | 186 | 1 | 11 | 0 | 30 | Max |  |  | 0.04 | 27.2 | 21.5 | 0 | 40.5 | 22.667 | 27.16 | 40.5 | 49.117
Compare | Concrete Heat Flux | Surface Temperature | 117 | 187 | 1 | 13 | 0 | 30 | Max |  |  | 0.0395 | 48.616 | 16.833 | 0 | 41.5 | 22.667 | 48.576 | 41.5 | -14.568
Compare | Light Concrete Heat Flux | Surface Temperature | 117 | 188 | 1 | 15 | 0 | 30 | Max |  |  | 0 | 32.398 | 25 | 0 | 40.4 | 22.667 | 32.398 | 40.4 | 24.698
Compare | Steel Heat Temperature | Surface Flux | 117 | 156 | 1 | 10 | 0 | 30 | Max |  |  | 19.5 | 376 | 25.333 | 20 | 403 | 23 | 356.5 | 383 | 7.4334
Compare | Concrete Heat Temperature | Surface Flux | 117 | 155 | 1 | 12 | 0 | 30 | Max |  |  | 18.8 | 327.5 | 23.333 | 20 | 461 | 22.833 | 308.7 | 441 | 42.857
Compare | Light Concrete Heat Temperature | Surface Flux | 117 | 151 | 1 | 14 | 0 | 30 | Max |  |  | 17.9 | 508.17 | 23.333 | 20 | 620 | 22.667 | 490.27 | 600 | 22.382
Compare | M19 Temperature | Surface Temperature | 117 | 139 | 1 | 16 | 0 | 30 | Max |  |  | 19.2 | 615 | 23 | 20 | 589 | 22.667 | 595.8 | 569 | -4.4981
Compare | M20 Temperature | Surface Temperature | 117 | 140 | 1 | 17 | 0 | 30 | Max |  |  | 19.3 | 742.5 | 22.833 | 20 | 281 | 23.333 | 723.2 | 261 | -63.91
Experiment | ICFMP5_Test_4 | 1
Model | ICFMP5_Test_4 | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | HGL Temperature | HGL Temperature | 125 | 168 | 1 | 2 | 0 | 20 | Max |  |  | 18.7 | 169 | 19.5 | 20 | 196 | 18.833 | 150.3 | 176 | 17.099
Compare | HGL Height | HGL Height | 125 | 170 | 1 | 3 | 5 | 20 | Min |  |  | 5.6 | 1.28 | 19 | 5.6 | 2.16 | 18.5 | -4.32 | -3.44 | -20.37
Compare | Oxygen | Oxygen | 125 | 293 | 1 | 5 | 0 | 20 | Min |  |  | 0.21 | 0.18617 | 19.833 | 0.205 | 0.185 | 16 | -0.023833 | -0.02 | -16.084
Compare | Carbon Dioxide | Carbon Dioxide | 125 | 295 | 1 | 6 | 0 | 20 | Max |  |  | 0.000541 | 0.01345 | 19.833 | 0 | 0.0117 | 19 | 0.012909 | 0.0117 | -9.3656
Compare | WS2 Flux | Cable Flux | 125 | 271 | 1 | 11 | 0 | 20 | Max |  |  | -0.01 | 3.6 | 20 | 0 | 1.89 | 19.333 | 3.61 | 1.89 | -47.645
Compare | WS 3 Flux | Cable Flux | 125 | 172 | 1 | 13 | 0 | 20 | Max |  |  | 0 | 96.9 | 20 | 0 | 2.74 | 19.667 | 96.9 | 2.74 | -97.172
Compare | WS 4 Flux | Cable Flux | 125 | 273 | 1 | 15 | 0 | 20 | Max |  |  | -0.01 | 5.7399 | 15.5 | 0 | 2.73 | 20 | 5.7499 | 2.73 | -52.521
Compare | TCO 1-3 Temperature | Cable Temperature | 125 | 199 | 1 | 18 | 0 | 20 | Max |  |  | 18.4 | 106 | 19.5 | 20 | 95 | 20 | 87.6 | 75 | -14.384
Compare | TCO 1-5 Temperature | Cable Temperature | 125 | 201 | 1 | 19 | 0 | 20 | Max |  |  | 18.8 | 128.83 | 19.333 | 20 | 113 | 20 | 110.03 | 93 | -15.48
Compare | TCO 1-7 Temperature | Cable Temperature | 125 | 203 | 1 | 20 | 0 | 20 | Max |  |  | 18.9 | 125.83 | 19.833 | 20 | 196 | 18.833 | 106.93 | 176 | 64.589
Compare | TCO 3-3 Temperature | Cable Temperature | 125 | 217 | 1 | 21 | 0 | 20 | Max |  |  | 18.5 | 130 | 19.333 | 20 | 114 | 19.667 | 111.5 | 94 | -15.695
Compare | TCO 3-5 Temperature | Cable Temperature | 125 | 219 | 1 | 22 | 0 | 20 | Max |  |  | 18.8 | 164.83 | 19.333 | 20 | 142 | 20 | 146.03 | 122 | -16.457
Compare | TCO 3-7 Temperature | Cable Temperature | 125 | 221 | 1 | 23 | 0 | 20 | Max |  |  | 19 | 159 | 19.667 | 20 | 140 | 20 | 140 | 120 | -14.286
Compare | TW 1-1 Temperature | Surface Temperature | 125 | 171 | 1 | 24 | 0 | 20 | Max |  |  | 18.7 | 74.9 | 20 | 20 | 59.9 | 20 | 56.2 | 39.9 | -29.004
Compare | TW 1-4 Temperature | Surface Temperature | 125 | 174 | 1 | 25 | 0 | 20 | Max |  |  | 18.9 | 106 | 19.667 | 20 | 59.1 | 20 | 87.1 | 39.1 | -55.109
Compare | TW 1-7 Temperature | Surface Temperature | 125 | 177 | 1 | 26 | 0 | 20 | Max |  |  | 18.8 | 104.83 | 19.833 | 20 | 59.5 | 20 | 86.033 | 39.5 | -54.088
Compare | TW 2-1 Temperature | Surface Temperature | 125 | 178 | 1 | 27 | 0 | 20 | Max |  |  | 17.7 | 22.2 | 20 | 20 | 47 | 20 | 4.5 | 27 | 500
Compare | TW 2-4 Temperature | Surface Temperature | 125 | 181 | 1 | 28 | 0 | 20 | Max |  |  | 19.2 | 87.167 | 19.833 | 20 | 57.6 | 20 | 67.967 | 37.6 | -44.679
Compare | TW 2-7 Temperature | Surface Temperature | 125 | 184 | 1 | 29 | 0 | 20 | Max |  |  | 19 | 91 | 20 | 20 | 59.2 | 20 | 72 | 39.2 | -45.556
Experiment | MV100A | 1
Model | MV100A | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Tree 1 HGL Temperature | HGL Temperature | 271 | 275 | 257 | 258 | 5 | 15 | Max |  |  | 23 | 282.39 | 14.667 | 23 | 260.43 | 14.833 | 259.39 | 237.43 | -8.467
Compare | Tree 1 HGL Height | HGL Height | 271 | 273 | 257 | 259 | 5 | 15 | Min |  |  | 2.16 | 0.89 | 8.8333 | 2.16 | 0.84134 | 5 | -1.27 | -1.3187 | 3.8318
Compare | Tree 4 HGL Temperature | HGL Temperature | 271 | 279 | 257 | 264 | 5 | 15 | Max |  |  | 23 | 109.16 | 14.667 | 23 | 111.06 | 14.833 | 86.16 | 88.057 | 2.2017
Compare | Tree 4 HGL Height | HGL Height | 271 | 277 | 257 | 265 | 5 | 15 | Min |  |  | 2.44 | 1.27 | 14.5 | 2.44 | 1.2542 | 5 | -1.17 | -1.1858 | 1.3471
Compare | Tree 5 HGL Temperature | HGL Temperature | 271 | 283 | 257 | 266 | 5 | 15 | Max |  |  | 23 | 100.28 | 14.333 | 23 | 111.06 | 14.833 | 77.28 | 88.057 | 13.946
Compare | Tree 5 HGL Height | HGL Height | 271 | 281 | 257 | 267 | 5 | 15 | Min |  |  | 2.44 | 1.15 | 14 | 2.44 | 1.2542 | 5 | -1.29 | -1.1858 | -8.0806
Compare | Tree 6 HGL Temperature | HGL Temperature | 271 | 287 | 257 | 268 | 5 | 15 | Max |  |  | 23 | 97.3 | 13.833 | 23 | 111.06 | 14.833 | 74.3 | 88.057 | 18.516
Compare | Tree 6 HGL Height | HGL Height | 271 | 285 | 257 | 269 | 5 | 15 | Min |  |  | 2.44 | 1.26 | 5.1667 | 2.44 | 1.2542 | 5 | -1.18 | -1.1858 | 0.48813
Experiment | MV100O | 1
Model | MV100O | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Tree 1 HGL Temperature | HGL Temperature | 280 | 284 | 266 | 267 | 5 | 15 | Max |  |  | 21 | 333 | 14.333 | 20 | 355.65 | 14.667 | 312 | 335.65 | 7.5805
Compare | Tree 1 HGL Height | HGL Height | 280 | 282 | 266 | 268 | 5 | 15 | Min | Closed |  | 2.16 | 0.84 | 9.6667 | 2.16 | 0.0036186 | 7.3333 | -1.32 | -2.1564
Compare | Tree 4 HGL Temperature | HGL Temperature | 280 | 288 | 266 | 273 | 5 | 15 | Max |  |  | 21 | 127.2 | 14.667 | 20 | 94.789 | 14.833 | 106.2 | 74.789 | -29.577
Compare | Tree 4 HGL Height | HGL Height | 280 | 286 | 266 | 274 | 5 | 15 | Min | Closed |  | 2.44 | 0.68 | 14.833 | 2.44 | 0.000244 | 6.8333 | -1.76 | -2.4398
Compare | Tree 5 HGL Temperature | HGL Temperature | 280 | 292 | 266 | 275 | 5 | 15 | Max |  |  | 21 | 120.33 | 14.667 | 20 | 94.789 | 14.833 | 99.33 | 74.789 | -24.706
Compare | Tree 5 HGL Height | HGL Height | 280 | 290 | 266 | 276 | 5 | 15 | Min | Closed |  | 2.44 | 0.52 | 14.833 | 2.44 | 0.000244 | 6.8333 | -1.92 | -2.4398
Compare | Tree 6 HGL Temperature | HGL Temperature | 280 | 296 | 266 | 277 | [5 empty] | 21 | [8 empty] | No experimental measureme
Compare | Tree 6 HGL Height | HGL Height | 280 | 294 | 266 | 278 | 5 | 15 | Min | Closed |  | 1.11 | 0.59 | 14.833 | 2.4398 | 0.000244 | 6.8333 | -0.52 | -2.4395
Experiment | MV100Z | 1
Model | MV100Z | 1
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Tree 1 HGL Temperature | HGL Temperature | 331 | 335 | 313 | 314 | 5 | 15 | Max |  |  | 22 | 307.67 | 13 | 22 | 262.33 | 14.833 | 285.67 | 240.33 | -15.873 | Experimental Peak = 282
Compare | Tree 1 HGL Height | HGL Height | 331 | 333 | 313 | 315 | 5 | 15 | Min |  |  | 2.16 | 0.82 | 9.6667 | 2.16 | 0.83962 | 5.1667 | -1.34 | -1.3204 | -1.464 | Experimental Peak = 1.0
Compare | Tree 4 HGL Temperature | HGL Temperature | 331 | 339 | 313 | 320 | 5 | 15 | Max |  |  | 22 | 89.08 | 14 | 22 | 85.776 | 14.833 | 67.08 | 63.776 | -4.9253
Compare | Tree 4 HGL Height | HGL Height | 331 | 337 | 313 | 321 | 5 | 15 | Min |  |  | 2.44 | 1.27 | 11.167 | 2.44 | 0.92512 | 5.3333 | -1.17 | -1.5149 | 29.477
Compare | Tree 5 HGL Temperature | HGL Temperature | 331 | 343 | 313 | 322 | 5 | 15 | Max |  |  | 22 | 89.22 | 14.667 | 22 | 85.776 | 14.833 | 67.22 | 63.776 | -5.1233
Compare | Tree 5 HGL Height | HGL Height | 331 | 341 | 313 | 323 | 5 | 15 | Min |  |  | 2.44 | 1.23 | 12.333 | 2.44 | 0.92512 | 5.3333 | -1.21 | -1.5149 | 25.197
Compare | Tree 7 HGL Temperature | HGL Temperature | 331 | 347 | 313 | 328 | 5 | 15 | Max |  |  | 22 | 58.59 | 14.833 | 22 | 55.473 | 14.833 | 36.59 | 33.473 | -8.5186
Compare | Tree 7 HGL Height | HGL Height | 331 | 345 | 313 | 329 | 5 | 15 | Min |  |  | 2.43 | 1.02 | 9.6667 | 2.43 | 0.34733 | 5.1667 | -1.41 | -2.0827 | 47.707
Experiment | NIST_Plaza | 3
Model | NIST_Plaza | 3
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Burn Room HGL Temperature | HGL Temperature | 1 | 2 | 10 | 11 | 0 | 30 | Max |  |  | 13.929 | 168.47 | 15.5 | 15 | 181.63 | 19.5 | 154.54 | 166.63 | 7.8258
Compare | Burn Room HGL Height | HGL Height | 1 | [17 empty] | No experimental measureme
Compare | Corridor HGL Temperature | HGL Temperature | 1 | 3 | 10 | 12 | 0 | 30 | Max |  |  | 15.338 | 439.36 | 13.5 | 15 | 402.76 | 19.5 | 424.02 | 387.76 | -8.5528
Compare | Corridor HGL Height | HGL Height | 1 | [17 empty] | No experimental measureme
Compare | Floor 7 HGL Temperature | HGL Temperature | 1 | 7 | 10 | 16 | 0 | 30 | Max |  |  | 14.586 | 15.168 | 24 | 15 | 17.28 | 19.5 | 0.582 | 2.2803 | 291.8
Compare | Floor 7 HGL Height | HGL Height | 1 | [17 empty] | No experimental measureme
Compare | Corridor Oxygen | Oxygen | 1 | 4 | 10 | 13 | 0 | 30 | Min |  |  | 20.9 | 9.87 | 14.5 | 20.544 | 12.165 | 19.5 | -11.03 | -8.3791 | -24.034
Compare | Corridor Carbon Dioxide | Carbon Dioxide | 1 | 6 | 10 | 15 | 0 | 30 | Max |  |  | 0 | 4.03 | 15 | 0 | 2.8657 | 19.5 | 4.03 | 2.8657 | -28.89
Compare | Corridor 7 Pressure | Pressure | 1 | 8 | 10 | 17 | 0 | 30 | Max |  |  | 1.9892 | 3.5834 | 6.5 | 9.5046 | 10.361 | 19.5 | 1.5942 | 0.85683 | -46.253
Experiment | fm19 | 5
Model | fm19 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 123 | 114 | 126 | 127 | 0 | 8 | Max |  |  | 21.7 | 265.83 | 7.8333 | 15 | 305.8 | 6.6667 | 244.13 | 290.8 | 19.114
Compare | Room 1 HGL Height | HGL Height | 123 | 14 | 126 | 128 | 0 | 8 | Min |  |  | 2.45 | 0.4885 | 3.1667 | 2.4498 | 1.0328 | 8 | -1.9615 | -1.417 | -27.759
Compare | Room 1 Oxygen | Oxygen | 123 | 20 | 126 | 130 | 0 | 8 | Min |  |  | 20.8 | 17.7 | 5.6667 | 20.545 | 15.718 | 8 | -3.1 | -4.8272 | 55.716
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 123 | 2 | 126 | 131 | 0 | 8 | Max |  |  | 0 | 2.2917 | 5.6667 | 0 | 2.5145 | 8 | 2.2917 | 2.5145 | 9.7246
Compare | Room 1 Pressure | Pressure | 123 |  | 126 | 129 | [14 empty] | No experimental measureme
Compare | Room 2 HGL Temperature | HGL Temperature | 123 | 115 | 126 | 132 | 0 | 8 | Max |  |  | 16.7 | 74.2 | 8 | 15 | 102.37 | 4.8333 | 57.5 | 87.372 | 51.951
Compare | Room 2 HGL Height | HGL Height | 123 | 11 | 126 | 133 | 0 | 8 | Min |  |  | 2.43 | 0.44 | 3.5 | 2.4298 | 0.13258 | 8 | -1.99 | -2.2972 | 15.436
Compare | Room 2 HGL Temperature | HGL Temperature | 123 | 116 | 126 | 132 | 0 | 8 | Max |  |  | 16.4 | 78.7 | 8 | 15 | 102.37 | 4.8333 | 62.3 | 87.372 | 40.244
Compare | Room 2 HGL Height | HGL Height | 123 | 12 | 126 | 133 | 0 | 8 | Min |  |  | 2.43 | 0.43901 | 2 | 2.4298 | 0.13258 | 8 | -1.991 | -2.2972 | 15.379
Compare | Room 2 HGL Temperature | HGL Temperature | 123 | 117 | 126 | 132 | 0 | 8 | Max |  |  | 17.2 | 97.3 | 8 | 15 | 102.37 | 4.8333 | 80.1 | 87.372 | 9.0789
Compare | Room 2 HGL Height | HGL Height | 123 | 13 | 126 | 133 | 0 | 8 | Min |  |  | 2.43 | 0.499 | 0 | 2.4298 | 0.13258 | 8 | -1.931 | -2.2972 | 18.963
Compare | Room 2 Oxygen | Oxygen | 123 | 19 | 126 | 135 | 0 | 8 | Min |  |  | 20.6 | 16.9 | 7.8333 | 20.544 | 17.377 | 8 | -3.7 | -3.1679 | -14.381
Compare | Room 2 Carbon Dioxide | Carbon Dioxide | 123 | 1 | 126 | 136 | 0 | 8 | Max |  |  | 0 | 2.05 | 8 | 0 | 1.648 | 8 | 2.05 | 1.648 | -19.611
Compare | Room 2 Pressure | Pressure | 123 |  | 126 | 134 | [14 empty] | No experimental measureme
Compare | Room 3 HGL Temperature | HGL Temperature | 123 | 118 | 126 | 137 | 0 | 8 | Max |  |  | 15.2 | 67.5 | 8 | 15 | 58.359 | 8 | 52.3 | 43.359 | -17.095
Compare | Room 3 HGL Height | HGL Height | 123 | 15 | 126 | 138 | 0 | 8 | Min |  |  | 2.45 | 0.46333 | 2.8333 | 2.4497 | 0.027278 | 8 | -1.9867 | -2.4225 | 21.937
Compare | Room 3 Carbon Dioxide | Carbon Dioxide | 123 | 3 | 126 | 141 | 0 | 8 | Max |  |  | 0 | 1.82 | 8 | 0 | 1.4857 | 8 | 1.82 | 1.4857 | -18.368
Compare | Room 3 Pressure | Pressure | 123 |  | 126 | 139 | [14 empty] | No experimental measureme
Compare | Room 4 HGL Temperature | HGL Temperature | 123 | 119 | 126 | 142 | 0 | 8 | Max |  |  | 15.3 | 52 | 8 | 15 | 59.145 | 8 | 36.7 | 44.145 | 20.287
Compare | Room 4 HGL Height | HGL Height | 123 | 16 | 126 | 143 | 0 | 8 | Min |  |  | 2.43 | 0.38 | 1 | 2.4298 | 0.025524 | 8 | -2.05 | -2.4042 | 17.28
Compare | Room 4 Carbon Dioxide | Carbon Dioxide | 123 | 4 | 126 | 146 | 0 | 8 | Max |  |  | 0 | 1.94 | 8 | 0 | 1.4966 | 8 | 1.94 | 1.4966 | -22.856
Compare | Room 4 Pressure | Pressure | 123 |  | 126 | 144 | [14 empty] | No experimental measureme
Experiment | fm21 | 5
Model | fm21 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 125 | 116 | 128 | 129 | 0 | 8 | Max |  |  | 15.5 | 360.83 | 7.8333 | 15 | 342.71 | 8 | 345.33 | 327.71 | -5.1039
Compare | Room 1 HGL Height | HGL Height | 125 | 16 | 128 | 130 | 0 | 8 | Min |  |  | 2.45 | 0.731 | 4.8333 | 2.4498 | 0.16287 | 8 | -1.719 | -2.2869 | 33.036
Compare | Room 1 Oxygen | Oxygen | 125 | 22 | 128 | 132 | 0 | 8 | Min |  |  | 22.5 | 16.5 | 7.8333 | 20.545 | 11.805 | 8 | -6 | -8.7408 | 45.68
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 125 | 4 | 128 | 133 | 0 | 8 | Max |  |  | 0 | 3.41 | 8 | 0 | 4.5009 | 8 | 3.41 | 4.5009 | 31.991
Compare | Room 1 Pressure | Pressure | 125 |  | 128 | 131 | [14 empty] | No experimental measureme
Compare | Room 2 HGL Temperature | HGL Temperature | 125 | 117 | 128 | 134 | 0 | 8 | Max |  |  | 13.2 | 97 | 8 | 15 | 118.64 | 8 | 83.8 | 103.64 | 23.672
Compare | Room 2 HGL Height | HGL Height | 125 | 13 | 128 | 135 | 0 | 8 | Min |  |  | 2.43 | 0.32118 | 0.83333 | 2.4298 | 0.018212 | 8 | -2.1088 | -2.4115 | 14.355
Compare | Room 2 HGL Temperature | HGL Temperature | 125 | 118 | 128 | 134 | 0 | 8 | Max |  |  | 13.1 | 106 | 8 | 15 | 118.64 | 8 | 92.9 | 103.64 | 11.557
Compare | Room 2 HGL Height | HGL Height | 125 | 14 | 128 | 135 | 0 | 8 | Min |  |  | 2.43 | 0.36 | 2.5 | 2.4298 | 0.018212 | 8 | -2.07 | -2.4115 | 16.5
Compare | Room 2 HGL Temperature | HGL Temperature | 125 | 119 | 128 | 134 | 0 | 8 | Max |  |  | 13.4 | 130 | 8 | 15 | 118.64 | 8 | 116.6 | 103.64 | -11.117
Compare | Room 2 HGL Height | HGL Height | 125 | 15 | 128 | 135 | 0 | 8 | Min |  |  | 2.43 | 0.40333 | 2.6667 | 2.4298 | 0.018212 | 8 | -2.0267 | -2.4115 | 18.991
Compare | Room 2 Oxygen | Oxygen | 125 | 21 | 128 | 137 | 0 | 8 | Min |  |  | 20.8 | 16.2 | 8 | 20.544 | 14.917 | 8 | -4.6 | -5.6278 | 22.343
Compare | Room 2 Carbon Dioxide | Carbon Dioxide | 125 | 1 | 128 | 138 | 0 | 8 | Max |  |  | 0 | 3.1 | 8 | 0 | 2.8982 | 8 | 3.1 | 2.8982 | -6.5088
Compare | Room 2 Carbon Dioxide | Carbon Dioxide | 125 | 2 | 128 | 138 | 0 | 8 | Max |  |  | 0 | 3.28 | 8 | 0 | 2.8982 | 8 | 3.28 | 2.8982 | -11.639
Compare | Room 2 Pressure | Pressure | 125 |  | 128 | 136 | [14 empty] | No experimental measureme
Compare | Room 3 HGL Temperature | HGL Temperature | 125 | 120 | 128 | 139 | 0 | 8 | Max |  |  | 13.2 | 88.4 | 8 | 15 | 74.688 | 8 | 75.2 | 59.688 | -20.627
Compare | Room 3 HGL Height | HGL Height | 125 | 17 | 128 | 140 | 0 | 8 | Min |  |  | 2.45 | 0.34 | 2.5 | 2.4497 | 0.00042219 | 8 | -2.11 | -2.4493 | 16.082
Compare | Room 3 Carbon Dioxide | Carbon Dioxide | 125 | 5 | 128 | 143 | 0 | 8 | Max |  |  | 0 | 2.87 | 8 | 0 | 2.4276 | 8 | 2.87 | 2.4276 | -15.415
Compare | Room 3 Pressure | Pressure | 125 |  | 128 | 141 | [14 empty] | No experimental measureme
Compare | Room 4 HGL Temperature | HGL Temperature | 125 | 120 | 128 | 144 | 0 | 8 | Max |  |  | 13.2 | 88.4 | 8 | 15 | 75.76 | 8 | 75.2 | 60.76 | -19.202
Compare | Room 4 HGL Height | HGL Height | 125 | 18 | 128 | 145 | 0 | 8 | Min |  |  | 2.43 | 0.32 | 1.5 | 2.4298 | 0.00031082 | 8 | -2.11 | -2.4294 | 15.14
Compare | Room 4 Carbon Dioxide | Carbon Dioxide | 125 | 6 | 128 | 148 | 0 | 8 | Max |  |  | 0 | 2.88 | 8 | 0 | 2.4549 | 8 | 2.88 | 2.4549 | -14.762
Compare | Room 4 Pressure | Pressure | 125 |  | 128 | 146 | [14 empty] | No experimental measureme
Experiment | 1Room1 | 5
Model | 1Room1 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature A | HGL Temperature | 87 | 85 | 109 | 110 | 0 | 30 | Max |  |  | 22 | 791.85 | 8.3333 | 27 | 754.93 | 8.5 | 769.85 | 727.93 | -5.4458
Compare | Room 1 HGL Height A | HGL Height | 87 | 11 | 109 | 111 | 0 | 30 | Min |  |  | 2.31 | 0.23858 | 7 | 2.3098 | 0.34278 | 8 | -2.0714 | -1.967 | -5.0415
Compare | Room 1 HGL Temperature B | HGL Temperature | 87 | 86 | 109 | 110 | 0 | 30 | Max |  |  | 23.58 | 919.25 | 7.5 | 27 | 754.93 | 8.5 | 895.67 | 727.93 | -18.728
Compare | Room 1 HGL Height B | HGL Height | 87 | 12 | 109 | 111 | 0 | 30 | Min |  |  | 2.31 | 0.081517 | 7 | 2.3098 | 0.34278 | 8 | -2.2285 | -1.967 | -11.734
Compare | Room 1 Oxygen A | Oxygen | 87 | 21 | 109 | 113 | 0 | 30 | Min |  |  | 20.9 | 0 | 8.1667 | 20.355 | 6.4442 | 8.1667 | -20.9 | -13.911 | -33.442
Compare | Room 1 Carbon Dioxide A | Carbon Dioxide | 87 | 3 | 109 | 114 | 0 | 30 | Max |  |  | 0 | 16.911 | 8 | 0 | 5.3877 | 8.1667 | 16.911 | 5.3877 | -68.141
Compare | Room 1 Oxygen B | Oxygen | 87 | 22 | 109 | 113 | 0 | 30 | Min |  |  | 20.9 | 1.3682 | 8.1667 | 20.355 | 6.4442 | 8.1667 | -19.532 | -13.911 | -28.779
Compare | Room 1 Carbon Dioxide B | Carbon Dioxide | 87 | 4 | 109 | 114 | 0 | 30 | Max |  |  | 0 | 16.153 | 8.1667 | 0 | 5.3877 | 8.1667 | 16.153 | 5.3877 | -66.646
Compare | Room 1 Pressure | Pressure | 87 |  | 109 | 112 | [14 empty] | No experimental measureme
Experiment | 1Room6 | 5
Model | 1Room6 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature A | HGL Temperature | 87 | 85 | 113 | 114 | 0 | 30 | Max |  |  | 23.43 | 587.35 | 8.5 | 27 | 636.34 | 8.6667 | 563.92 | 609.34 | 8.055
Compare | Room 1 HGL Height A | HGL Height | 87 | 11 | 113 | 115 | 0 | 30 | Min |  |  | 2.31 | 0.076499 | 0.16667 | 2.3098 | 0.49368 | 8.5 | -2.2335 | -1.8161 | -18.689
Compare | Room 1 HGL Temperature B | HGL Temperature | 87 | 86 | 113 | 114 | 0 | 30 | Max |  |  | 25.88 | 901.75 | 8.5 | 27 | 636.34 | 8.6667 | 875.87 | 609.34 | -30.43
Compare | Room 1 HGL Height B | HGL Height | 87 | 12 | 113 | 115 | 0 | 30 | Min |  |  | 2.31 | 0.86982 | 7.6667 | 2.3098 | 0.49368 | 8.5 | -1.4402 | -1.8161 | 26.102
Compare | Room 1 Oxygen A | Oxygen | 87 | 21 | 113 | 117 | 0 | 30 | Min |  |  | 20.9 | 6.8713 | 8.1667 | 20.355 | 10.262 | 8.5 | -14.029 | -10.093 | -28.053
Compare | Room 1 Carbon Dioxide A | Carbon Dioxide | 87 | 3 | 113 | 118 | 0 | 30 | Max |  |  | 0 | 10.602 | 8.1667 | 0 | 3.9471 | 8.5 | 10.602 | 3.9471 | -62.77
Compare | Room 1 Oxygen B | Oxygen | 87 | 22 | 113 | 117 | 0 | 30 | Min |  |  | 20.9 | 10.995 | 8.1667 | 20.355 | 10.262 | 8.5 | -9.905 | -10.093 | 1.9001
Compare | Room 1 Carbon Dioxide B | Carbon Dioxide | 87 | 4 | 113 | 118 | 0 | 30 | Max |  |  | 0 | 8.1104 | 8 | 0 | 3.9471 | 8.5 | 8.1104 | 3.9471 | -51.333
Compare | Room 1 Pressure | Pressure | 87 |  | 113 | 116 | [14 empty] | No experimental measureme
Experiment | 1RWall1 | 5
Model | 1RWall1 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 83 | 82 | 110 | 111 | 0 | 30 | Max |  |  | 24.5 | 801.5 | 11.833 | 22 | 611.37 | 3.8333 | 777 | 589.37 | -24.148
Compare | Room 1 HGL Height | HGL Height | 83 | 8 | 110 | 112 | 0 | 30 | Min |  |  | 2.44 | 0.20883 | 11.833 | 2.4398 | 0.72896 | 3.6667 | -2.2312 | -1.7108 | -23.323
Compare | Room 1 Oxygen | Oxygen | 83 |  | 110 | 114
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 83 |  | 110 | 115 | [5 empty] | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 83 | 32 | 110 | 113 | 0 | 30 | Min |  |  | -0.0249 | -1.865 | 12.167 | 0 | -4.689 | 3.8333 | -1.8401 | -4.689 | 154.82
Experiment | 1RWall2 | 5
Model | 1RWall2 | 5
|  |  | Exp Time | Exp Meas | Mod Time | Mod Meas | Beg Time | End Time | Min or Max | Opening |  | Exp Zero | Exp Peak | Peak Time | Mod Zero | Mod Peak | Peak Time | DeltaE | DeltaM | Rel Diff
Compare | Room 1 HGL Temperature | HGL Temperature | 105 | 104 | 133 | 134 | 0 | 10 | Max |  |  | 23.37 | 806.75 | 8.6667 | 22 | 1215.1 | 7.3333 | 783.38 | 1193.1 | 52.305
Compare | Room 1 HGL Height | HGL Height | 105 | 8 | 133 | 135 | 0 | 10 | Min |  |  | 2.44 | 0.11027 | 8.3333 | 2.4398 | 0.6236 | 6.5 | -2.3297 | -1.8162 | -22.044
Compare | Room 1 Oxygen | Oxygen | 105 |  | 133 | 137
Compare | Room 1 Carbon Dioxide | Carbon Dioxide | 105 |  | 133 | 138 | [5 empty] | 0 |  |  | 0
Compare | Room 1 Pressure | Pressure | 105 | 32 | 133 | 136 | 0 | 10 | Min |  |  | -0.17409 | -1.8901 | 8.6667 | 0 | -6.5486 | 7.6667 | -1.716 | -6.5486 | 281.62
End

## Mod vs Exp
[29 empty] | 14% | 13% | 16% | 14% | 9% | 33% | 40% | 20% | 14%
Series | Meas HGl Temp | Pred HGL Temp | Meas HGL Depth | Pred HGL Depth | Meas Jet Temp | Pred Jet Temp | Meas Plume Temp | Pred Plume Temp | Meas CO2 | Pred CO2 | Meas O2 | Pred O2 | Meas Smoke | Pred Smoke | Meas Press | Pred Press | Meas Cable Temp | Pred Cable Temp | Meas Cable Rad | Pred Cable Rad | Meas Cable Flux | Pred Cable Flux | Meas Surface Temp | Pred Surface Temp | Meas Surface Flux | Pred Surface Flux | X Error Bars | 45° line | HGT Uncert | HGT Depth Uncert | Jet Uncert | Plume Temp Uncert | Gas Concen Uncert | Smoke Uncert | Pressure Uncert | Surface Flux Uncert | Surface Temp Uncert
VTT | 54.8 | 62.3 |  |  |  |  | 166 | 174 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 86 | 99 |  |  |  |  | 77 | 105 | [18 empty] | 1300 | 1300 | 1482 | 1469 | 1508 | 1482 | 1417 | 1729 | 1820 | 1560 | 1482
[7 empty] | 288 | 244
[7 empty] | 128 | 161 | [18 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 252 | 238 | [18 empty] | 1300 |  | 1118 | 1131 | 1092 | 1118 | 1183 | 871 | 780 | 1040 | 1118
| 82.5 | 91 | 13.86 | 14.94 |  |  | 128 | 141
NIST/NRC | 122.93 | 135.48 |  |  | 154.57 | 135.48 |  |  | 0.0384 | 0.044428 | 0.065 | 0.076111 | 41.467 | 320.45 | 57.522 | 42.398 | 106.4 | 102.77 | 1.1198 | 2.32 | 1.8446 | 2.46 | 54.183 | 88.943 | 1.3844 | 1.96 | 0 | [7 empty] | 0
| 116.8 | 133 |  |  | 139.07 | 133 |  |  | 0.037983 | 0.0426 | 0.064 | 0.073 | 55.05 | 307 | 45.882 | 28.8 |  |  | 1.4394 | 1.5 |  |  | 67.967 | 88.993 | 1.7656 | 1.95 | -1300 | [7 empty] | -1820
| 229 | 234.57 |  |  | 270.46 | 234.57 |  |  | 0.05455 | 0.058654 | 0.092333 | 0.10048 | 128 | 419.47 | 290 | 266.05 | 82.6 | 67.853 | 0.86659 | 1.36 | 1.5926 | 2.37 | 55.317 | 88.512 | 1.255 | 1.96
| 218.2 | 234 |  |  | 247.24 | 234 |  |  | 0.057817 | 0.0574 | 0.095833 | 0.098 | 99.5 | 411 | 189 | 214 | 64.317 | 95.955 | 1.5094 | 1.51 |  |  | 70.95 | 89.118 | 1.7178 | 1.96 | 0 | [7 empty] | 0
| 204.2 | 222 |  |  | 227.7 | 222 |  |  | 0.04735 | 0.035 | 0.078 | 0.06 | 79.892 | 177 | 56.6 | 76.8 | 109.5 | 102 | 1.2072 | 2.27 | 1.8421 | 2.4 | 38.2 | 70.94 | 0.9244 | 1.68 | -1300 | [7 empty] | -780
| 198.3 | 221 |  |  | 217 | 221 |  |  | 0.046433 | 0.0347 | 0.078833 | 0.06 | 70.684 | 177 | 49.267 | 45.7 | 87.7 | 102 | 1.3491 | 1.47 | 2.5188 | 2.4467 | 77.383 | 69.215 | 2.3877 | 1.65
| 290.24 | 311 |  |  | 330.05 | 311 |  |  | 0.059988 | 0.0644 | 0.1008 | 0.1097 | 223.73 | 480 | 232 | 336 | 90.1 | 73.3 | 0.81985 | 1.33 | 1.5004 | 2.31 | 80.7 | 91.93 | 1.9244 | 2.21
| 268.46 | 290 |  |  | 277.3 | 290 |  |  | 0.05518 | 0.043817 | 0.090941 | 0.075 | 139 | 205 | 80.529 | 225 | 77.9 | 93 | 1.4664 | 1.48 | 1.8913 | 2.21 | 176.13 | 90.611 | 3.7535 | 2.17
| 135.3 | 143 |  |  | 155.4 | 143 |  |  | 0.021576 | 0.0166 | 0.032961 | 0.031 | 352.84 | 1590 | 194.82 | 137 | 175.37 | 143.98 | 2.8818 | 5.37 | 5.2517 | 5.77 | 53.1 | 87 | 1.3747 | 1.92
| 207.2 | 243 | 2.91 | 2.81 | 240.4 | 243 |  |  | 0.0311 | 0.0273 | 0.052 | 0.044 | 117.5 | 140 | -1.91 | -2.1 | 124.3 | 145.47 | 4.0262 | 4.12 | 9.3142 | 5.91 | 70.283 | 87 | 1.8779 | 1.9
| 204.13 | 241 | 2.92 | 2.8 | 234.1 | 241 |  |  | 0.0313 | 0.0269 | 0.053833 | 0.042 | 116 | 139 | -1.9467 | -2.1 | 128.57 | 112.25 | 1.9867 | 3.71 | 4.6796 | 5.51 | 54.567 | 86 | 1.2252 | 1.92
| 175.83 | 198 | 2.9483 | 2.66 | 207.07 | 198 |  |  | 0.0175 | 0.0161 | 0.03 | 0.026 | 87.033 | 90.6 | -1.81 | -1.96 | 106.6 | 138.22 | 5.9673 | 4.12 |  |  | 70.183 | 87 | 1.785 | 1.92
| 207.7 | 242 | 2.91 | 2.81 | 240.8 | 242 |  |  | 0.0322 | 0.0271 | 0.055 | 0.042 | 91.3 | 139 | -2.0367 | -2.12 | 183.1 | 142 | 2.9151 | 5.33 | 5.5811 | 5.73 | 36.3 | 68.6 | 0.9018 | 1.64
| 210.2 | 242 | 2.89 | 2.79 | 243.8 | 242 |  |  | 0.0312 | 0.0267 | 0.051 | 0.042 | 124 | 140 | -2.325 | -2.2 | 149.6 | 143 | 3.5563 | 4.07 | 8.4749 | 5.87 | 78.167 | 66.9 | 2.3174 | 1.6
| 193.33 | 243 | 2.91 | -2.81 | 234.7 | 243 |  |  | 0.0306 | 0.0272 | 0.05 | 0.044 | 109.5 | 140 | -2.01 | -2.15 | 131.3 | 111 | 1.9294 | 3.66 | 4.907 | 5.46 | 80.4 | 89.333 | 1.9419 | 2.15
[17 empty] | 106.4 | 136 | 6.0171 | 4.08 | 5.9798 | 5.44 | 191.3 | 88
[17 empty] | 147.97 | 156 | 2.909 | 4.96 | 5.5228 | 5.36 | 95.433 | 150.35 | 3.7791 | 4.65
[17 empty] | 112.63 | 157 | 3.2523 | 3.8 | 7.232 | 5.49 | 120.1 | 151.35 | 4.5046 | 4.61
[17 empty] | 147.93 | 115 | 2.0209 | 3.43 | 5.0203 | 5.12 | 109.43 | 149.77 | 3.5887 | 4.64
[17 empty] | 124.53 | 149 | 5.9979 | 3.79 | 6.3937 | 5.07 | 125.4 | 150.61 | 4.6104 | 4.64
[17 empty] | 143.5 | 161.67 | 2.6752 | 4.9267 | 4.8356 | 5.33 | 74.083 | 127.01 | 2.5789 | 4.17
[17 empty] | 131.87 | 163 | 2.9163 | 3.77 | 6.6501 | 5.46 | 156.2 | 123.54 | 8.8987 | 4.06
[17 empty] | 150 | 128 | 1.9192 | 3.4 | 4.3199 | 5.09 | 147.8 | 154.15 | 5.6479 | 5.08
[17 empty] | 147.97 | 149 | 5.4231 | 3.76 | 6.201 | 5.03 | 307.89 | 152.02 | 14.479 | 4.97
[17 empty] | 185.46 | 165 | 4.7675 | 8.88 | 8.2506 | 9.67 | 95.1 | 149 | 3.8412 | 4.61
[17 empty] | 173.5 | 168 | 6.5743 | 7.58 | 11.258 | 9.95 | 131.87 | 150 | 3.211 | 4.57
[17 empty] | 143.38 | 143 | 2.9006 | 6.79 | 7.2733 | 9.15 | 108.6 | 148 | 2.464 | 4.6067
[17 empty] | 132.9 | 164 | 10.1 | 7.6 | 12.086 | 9.38 | 124.67 | 149 | 4.702 | 4.6
[17 empty] | 160.1 | 166 | 4.1078 | 7.6717 | 8.3467 | 8.4517 | 71.2 | 125 | 2.5541 | 4.12
[17 empty] | 155.11 | 170 | 4.8232 | 6.4717 | 11.686 | 8.7017 | 148.2 | 121 | 8.6308 | 4.01
[17 empty] | 168.2 | 148 | 2.7569 | 5.7417 | 6.139 | 7.9717 | 147.23 | 152.67 | 6.13 | 5.0467
[17 empty] | 169.46 | 150.17 | 11.975 | 6.4517 | 12.177 | 8.1417 | 325.1 | 150.67 | 12.958 | 4.9367
[19 empty] | 1.301 | 2.5 | 2.3604 | 3.03 | 97.133 | 150 | 3.4053 | 4.25
[19 empty] | 1.5189 | 2.09 | 3.2783 | 3.14 | 145.3 | 152 | 3.5061 | 4.26
[19 empty] | 0.88175 | 1.76 | 1.854 | 2.82 | 105.8 | 149 | 3.256 | 4.25
[19 empty] | 2.4161 | 2.18 | 3.0607 | 2.94 | 120.6 | 150 | 3.9791 | 4.25
[17 empty] | 226 | 221 | 4.441 | 5.64 | 7.0924 | 6.48 | 76.283 | 130 | 2.4679 | 3.89
[17 empty] | 209.93 | 223 |  |  | 9.4535 | 6.65 | 151.6 | 127 | 8.5064 | 3.8
[17 empty] | 194.9 | 160 | 2.9453 | 4.3 | 5.5069 | 6.15 | 147.17 | 153 | 5.0427 | 4.66
[17 empty] | 169 | 224 | 5.3546 | 5.2 | 6.4465 | 6.6 | 180.1 | 153 | 6.0174 | 4.63
[17 empty] | 227.5 | 218 | 4.2854 | 5.47 | 6.5776 | 6.3 | 94.1 | 150 | 3.3386 | 4.23
[17 empty] | 220.4 | 219 | 5.2448 | 4.62 | 9.0579 | 6.46 | 161.7 | 151 | 3.4799 | 4.23
[17 empty] | 194.6 | 156 | 2.7315 | 4.13 | 5.08 | 5.97 | 106 | 149 | 3.1048 | 4.2267
[17 empty] | 166.4 | 221 | 5.1539 | 5.02 | 6.3506 | 6.41 | 116.9 | 150 | 3.875 | 4.22
[17 empty] | 149.63 | 183 | 3.8815 | 4.05 | 6.7987 | 4.93 | 71.1 | 129.67 | 2.2712 | 3.85
[17 empty] | 132.5 | 184 | 4.7706 | 3.56 | 8.493 | 5.06 | 155.87 | 126.67 | 7.893 | 3.77
[17 empty] | 174.7 | 128 | 2.6384 | 3.15 | 6.4535 | 4.65 | 137.87 | 153 | 4.7187 | 4.63
[17 empty] | 161.1 | 190 | 5.4496 | 4.01 | 6.689 | 5.15 | 221.16 | 152
[17 empty] | 199 | 207 | 2.8331 | 5.54 | 3.8193 | 5.78 | 110.38 | 195
[17 empty] | 178.3 | 208 |  |  | 6.0532 | 5.94 | 199.2 | 198
[17 empty] | 171.2 | 145 | 2.1155 | 3.68 | 3.4436 | 5.52 | 126.8 | 194
[17 empty] | 269.9 | 262 | 10.501 | 6.92 | 10.834 | 8.32 | 144.6 | 195
[17 empty] | 415.1 | 207 | 46.395 | 5.3333 | 57.758 | 5.58 | 89.58 | 166
[17 empty] | 243.1 | 209 |  |  | 20.893 | 5.74 | 148.3 | 161
[17 empty] | 669.9 | 155 | 18.165 | 3.43 | 23.94 | 5.33 | 319.03 | 196
[17 empty] | 161.33 | 263 | 3.7353 | 6.7 | 5.0773 | 8.14 | 497.44 | 197
[17 empty] | 235.5 | 227 | 5.2068 | 5.57 | 7.5725 | 6.71 | 107.3 | 175.17
[17 empty] | 217.2 | 222 |  |  | 7.8059 | 6.56 | 217.06 | 180.17
[17 empty] | 231.73 | 188 | 5.1423 | 5.43 | 8.6705 | 7.29 | 123 | 175
[19 empty] | 2.8431 | 4.17 | 4.4522 | 5.57 | 141.1 | 176
[21 empty] | 27.16 | 40.5 | 79.992 | 148.17
[21 empty] | 48.576 | 41.5 | 145.5 | 144
[21 empty] | 32.398 | 40.4 | 283.2 | 178
[21 empty] | 3.61 | 1.89 | 441.44 | 180
[23 empty] | 39 | 52.9 | 1.4667 | 2.16
[21 empty] | 96.9 | 2.74 | 82 | 65.2 | 0.9286 | 2.36
[23 empty] | 56.363 | 51.6 | 1.5629 | 2.15
[21 empty] | 5.7499 | 2.73 | 60.965 | 54.017 | 1.8988 | 2.16
[23 empty] | 24.4 | 34.1 | 0.85669 | 1.4
[23 empty] | 51.9 | 32.5 | 1.4977 | 1.35
[23 empty] | 68.673 | 57.717
[23 empty] | 229.76 | 64.3
[23 empty] | 114.6 | 187 | 3.4952 | 4.83
[23 empty] | 172 | 203 | 4.3188 | 5.32
[23 empty] | 86.9 | 152 | 2.5274 | 3.48
[23 empty] | 145.6 | 191 | 4.4423 | 4.94
[23 empty] | 53.6 | 143 | 1.9674 | 3.58
[23 empty] | 118.3 | 139 | 4.0486 | 3.46
[23 empty] | 155.33 | 194 | 4.5867 | 5.43
[23 empty] | 287.1 | 197 | 9.7624 | 5.54
[23 empty] | 112.9 | 184 | 3.4167 | 4.68
[23 empty] | 177.73 | 200 | 4.2022 | 5.17
[23 empty] | 87.933 | 148 | 2.3913 | 3.34
[23 empty] | 134.73 | 188
[23 empty] | 53.083 | 139 | 1.9126 | 3.43
[23 empty] | 121.8 | 135 | 3.8607 | 3.31
[23 empty] | 203.6 | 191 | 5.453 | 5.27
[23 empty] | 289.9 | 194 | 9.403 | 5.39
[23 empty] | 93.7 | 146 | 2.6754 | 3.46
[23 empty] | 154.4 | 168 | 3.8164 | 4.06
[23 empty] | 71.117 | 116 | 1.9808 | 2.48
[23 empty] | 117.5 | 148 | 3.2916 | 3.51
[23 empty] | 41.6 | 107 | 1.3953 | 2.48
[23 empty] | 171 | 104 | 10.011 | 2.41
[23 empty] | 124.9 | 151 | 3.3587 | 3.9
[23 empty] | 263.2 | 159 | 6.7404 | 4.11
[23 empty] | 114.4 | 184 | 3.4901 | 4.7
[23 empty] | 254.37 | 222 | 8.1 | 5.9
[23 empty] | 86.8 | 149 | 2.3421 | 3.4
[23 empty] | 147.6 | 189 | 4.4688 | 4.84
[23 empty] | 52.2 | 141 | 1.8899 | 3.49
[23 empty] | 103.8 | 137 | 2.9711 | 3.37
[23 empty] | 157.7 | 192 | 4.683 | 5.33
[23 empty] | 350.63 | 200 | 8.9956 | 5.6
[23 empty] | 219.2 | 183 | 3.6362 | 4.54
[23 empty] | 205.2 | 188 | 7.4526 | 4.67
[23 empty] | 95.8 | 145 | 2.5828 | 3.2
[23 empty] | 151 | 187 | 4.6511 | 4.66
[23 empty] | 52.233 | 137 | 1.9428 | 3.26
[23 empty] | 131.1 | 132 | 5.1714 | 3.15
[23 empty] | 157 | 191
[23 empty] | 287.1 | 186
[23 empty] | 118.1 | 185 | 3.3999 | 4.68
[23 empty] | 312.53 | 248
[23 empty] | 93.8 | 154 | 2.5491 | 3.43
[23 empty] | 152.6 | 190 | 4.6567 | 4.88
[23 empty] | 49.533 | 141 | 1.7892 | 3.5
[23 empty] | 106.2 | 137 | 3.0577 | 3.38
[23 empty] | 144.6 | 193 | 4.4763 | 5.35
[23 empty] | 249.63 | 194
[23 empty] | 595.8 | 569
[23 empty] | 723.2 | 261
[23 empty] | 56.2 | 39.9
[23 empty] | 4.5 | 27
[23 empty] | 87.1 | 39.1
[23 empty] | 67.967 | 37.6
[23 empty] | 86.033 | 39.5
[23 empty] | 72 | 39.2
iBMB | 700.4 | 618 | 4.2 | 5.08 | [12 empty] | 356.5 | 383 |  |  | 27.16 | 40.5 | 595.8 | 569
[17 empty] | 308.7 | 441 |  |  | 48.576 | 41.5 | 723.2 | 261
[17 empty] | 490.27 | 600 |  |  | 32.398 | 40.4
iBMB | 150.3 | 176 | 4.32 | 3.44 |  |  |  |  | 0.012909 | 0.0117 | 0.023833 | 0.02 |  |  |  |  | 87.6 | 75 |  |  | 3.61 | 1.89 | 56.2 | 39.9
[17 empty] | 111.5 | 94 |  |  |  |  | 4.5 | 27
[17 empty] | 110.03 | 93 |  |  | 96.9 | 2.74 | 87.1 | 39.1
[17 empty] | 146.03 | 122 |  |  |  |  | 67.967 | 37.6
[17 empty] | 106.93 | 176 |  |  | 5.7499 | 2.73 | 86.033 | 39.5
[17 empty] | 140 | 120 |  |  |  |  | 72 | 39.2
FM SNL | 59 | 68.938 |  |  | 82.18 | 133.49 | 114.2 | 137
| 44.223 | 49.21 |  |  | 65.78 | 102.45 | 93.402 | 112
| 66 | 87.966 |  |  | 70.419 | 101 | 79 | 186
[5 empty] | 52.56 | 75
[5 empty] | 74.833 | 159
[5 empty] | 76.9 | 124.3
FM NBS | 244.13 | 290.8 | 1.9615 | 1.417 |  |  |  |  | 0.022917 | 0.025145 | 0.031 | 0.048272
| 57.5 | 87.372 | 1.99 | 2.2972 |  |  |  |  | 0.0205 | 0.01648 | 0.037 | 0.031679
| 62.3 | 87.372 | 1.991 | 2.2972 |  |  |  |  | 0.0182 | 0.014857
| 80.1 | 87.372 | 1.931 | 2.2972 |  |  |  |  | 0.0194 | 0.014966
| 52.3 | 43.359 | 1.9867 | 2.4225 |  |  |  |  | 0.0341 | 0.045009 | 0.06 | 0.087408
| 44.145 | 20.287 | 2.05 | 2.4042 |  |  |  |  | 0.031 | 0.028982 | 0.046 | 0.056278
| 345.33 | 327.71 | 1.719 | 2.2869 |  |  |  |  | 0.0328 | 0.028982
| 83.8 | 103.64 | 2.1088 | 2.4115 |  |  |  |  | 0.0287 | 0.024276
| 92.9 | 103.64 | 2.07 | 2.4115
| 116.6 | 103.64 | 2.0267 | 2.4115
| 75.2 | 59.688 | 2.11 | 2.4493
| 75.2 | 60.76 | 2.11 | 2.4294
NBS | 259.39 | 237.43 | 1.27 | 1.3187 |  |  |  |  | 0.209 | 0.13911 | 0.16911 | 0.053877 |  |  | -1.8401 | -4.689
| 86.16 | 88.057 | 1.17 | 1.1858 |  |  |  |  | 0.19532 | 0.13911 | 0.16153 | 0.053877 |  |  | -1.716 | -6.5486
| 77.28 | 88.057 | 1.29 | 1.1858 |  |  |  |  | 0.14029 | 0.10093 | 0.10602 | 0.039471
| 74.3 | 88.057 | 1.18 | 1.1858 |  |  |  |  | 0.09905 | 0.10093 | 0.081104 | 0.039471
| 312 | 335.65
| 106.2 | 74.789
| 99.33 | 74.789
| 285.67 | 240.33 | 1.34 | 1.3204
| 67.08 | 63.776 | 1.17 | 1.5149
| 67.22 | 63.776 | 1.21 | 1.5149
| 36.59 | 33.473 | 1.41 | 2.0827
| 769.85 | 727.93 | 2.0714 | 1.967
| 895.67 | 727.93 | 2.2285 | 1.967
| 563.92 | 609.34 | 2.2335 | 1.8161
| 875.87 | 609.34 | 1.4402 | 1.8161
| 777 | 589.37 | 2.2312 | 1.7108
| 783.38 | 1193.1 | 2.3297 | 1.8162
NIST Plaza | 154.54 | 166.63 | [6 empty] | 0.0403 | 0.028657 | 0.1103 | 0.083791
| 424.02 | 387.76
| 0.582 | 2.2803
NIST High Bay | [6 empty] | 32 | 42.562
[7 empty] | 29 | 38.3698
[7 empty] | 46 | 51.8042
[7 empty] | 79 | 90.2325
[7 empty] | 127 | 144.8501
[7 empty] | 119 | 131.7518
[7 empty] | 55 | 64.4562
[7 empty] | 130 | 140.4073
[7 empty] | 234 | 244.4064

## Rel Diffs
[60 empty] | 14% | 13% | 16% | 14% | 9% | 33% | 40% | 20% | 14%
| HGL Temp | [5 empty] | HGL Depth | [5 empty] | Ceiling Jet Temp |  | Plume Temp |  | CO2 |  |  |  |  | O2 |  | Smoke |  | Press | Cable Temp | [5 empty] | Cable Rad |  |  |  | Cable Flux |  |  |  |  | Surface Temp | [7 empty] | Surface Flux | [7 empty] | For Category Axis | X Error Bars | HGT Uncert | HGT Depth Uncert | Jet Uncert | Plume Temp Uncert | Gas Concen Uncert | Smoke Uncert | Pressure Uncert | Surface Flux Uncert | Surface Temp Uncert
VTT 1 | 13.686 | [13 empty] | 4.8193 | 36.364 | [41 empty] | 0 | 0 | 14 | 13 | 16 | 14 | 9 | 33 | 40 | 20 | 14
VTT 2 | 15.116 | [13 empty] | -15.278 | 25.781 | [41 empty] | 0 | 35 | 14 | 13 | 16 | 14 | 9 | 33 | 40 | 20 | 14
VTT 3 | 10.303 | [5 empty] | 7.7922 | [7 empty] | -5.5556 | 10.156 | [41 empty] | 0
NIST/NRC 1 | 10.207 | [11 empty] | -12.348 |  |  |  | 15.697 |  |  |  |  | 17.094 |  | 672.79 |  | -26.292 | -3.4107 |  | -17.854 | 49.191 |  |  | 107.18 | 4.2131 | 56.938 | 0.040232 | 33.359 |  | 48.81 |  |  | 64.152 | 30.936 | 60.009 | 25.607 | 85.708 | -10.556 | 13.916 | -48.555 | 41.578 | 10.442 | 56.169 | 14.1 | 81.74 | -30.896 | 14.841 | -42.188 | 0 | 0 | -14 | -13 | -16 | -14 | -9 | -33 | -40 | -20 | -14
NIST/NRC 7 | 13.87 | [11 empty] | -4.3625 |  |  |  | 12.154 |  |  |  |  | 14.062 |  | 457.67 |  | -37.231 | -6.8493 | 16.306 | -18.646 | 19.384 |  |  | 88.031 | 8.9608 | 62.224 | 0.92903 | 30.284 | -2.8634 | 53.961 | 16.851 |  | 63.842 | 23.785 | 57.605 | 23.961 | 88.981 | -14.414 | 11.111 | -53.999 | 39.663 | 1.1783 | 56.709 | 7.563 | 81.859 | -30.959 | 10.719 |  | 0 | 35 | -14 | -13 | -16 | -14 | -9 | -33 | -40 | -20 | -14
NIST/NRC 2 | 2.4336 | [11 empty] | -13.27 |  |  |  | 7.5225 |  |  |  |  | 8.8264 |  | 227.71 |  | -8.2593 | -17.898 | 17.033 | -12.69 | 29.665 |  |  | 86.34 | 2.3294 | 86.741 | -30.957 | 9.8698 | -36.548 | 17.745 |  |  | 57.546 | 26.02 | 36.862 | 20.106 | 71.445 | -20.911 | 4.2977 | -50.625 | 23.045 | 2.3391 | 29.295 | 0.64202 | 61.697 | -54.376 | -10.055 | -65.673 | 0
NIST/NRC 8 | 7.2411 | [11 empty] | -5.3556 |  |  |  | -0.72067 |  |  |  |  | 2.2609 |  | 313.07 |  | 13.227 | -22.447 | -4.4118 | -15.461 | 27.82 |  |  | 82.84 | 14.446 | 89.7 | -32.193 | 2.6679 | -30.736 | 11.27 | -9.0277 |  | 56.677 | 13.751 | 36.28 | 19.519 | 75.562 | -18.354 | 3.6903 | -53.655 | 20.015 | 42.325 | 86.959 | -2.17 | 61.309 | -53.538 | -17.673 | -61.903 | 0
NIST/NRC 4 | 8.7169 | [11 empty] | -2.5033 |  |  |  | -26.082 |  |  |  |  | -23.077 |  | 121.55 |  | 35.689 | 5.429 | 39.39 | -22.262 | 19.647 |  |  | 70.504 | 16.84 | 69.724 | -36.811 | -2.9476 | -24.087 | 1.9861 | -20.703 |  | 54.427 | 4.6112 | 40.832 | 24.378 | 70.417 | -16.227 | 3.9637 | -15.047 | 24.807 | 21.503 | 30.529 | 6.8082 | 57.622 | -55.328 | -7.5893 | -23.057 | 0
NIST/NRC 10 | 11.447 | [11 empty] | 1.8434 |  |  |  | -25.269 |  |  |  |  | -23.89 |  | 150.41 |  | -7.2395 | 12.66 | 23.61 | -14.667 | 0.6984 |  |  | 84.158 | 29.271 | 77.158 | -30.666 | 10.223 | -17.896 | 17.826 | -18.884 |  | 59.405 | -6.6173 | 40.566 | 28.315 | 82.372 | -18.734 | 10.977 | -31.272 | 26.701 | 21.554 | 36.135 | 8.9041 | 69.514 | -52.236 | -1.8794 |  | 0
NIST/NRC 13 | 7.1515 | [11 empty] | -5.7716 |  |  |  | 7.3545 |  |  |  |  | 8.8252 |  | 114.55 |  | 44.828 | -11.032 | -3.17 | -0.26536 | 23.401 |  |  | 86.26 | 15.297 | 134.09 | -24.754 | 17.204 | -11.621 | 25.803 | -22.387 |  | 76.662 | -0.60243 | 52.997 | 34.855 | 85.308 | 8.5637 | -38.563 | -60.397 | [8 empty] | 0
NIST/NRC 16 | 8.0224 | [11 empty] | 4.5799 |  |  |  | -20.594 |  |  |  |  | -17.529 |  | 47.482 |  | 179.4 | 3.6852 | 9.5999 | -12.01 | -11.386 |  |  | 86.76 | 34.178 | 108.26 | -46.124 | 1.2574 | -25.537 | 29.853 | -33.141 |  | 63.249 | -16.997 | 42.276 | 24.734 | 85.226 | -1.0309 | -37.147 | -59.225 | [8 empty] | 0
NIST/NRC 17 | 5.6911 | [11 empty] | -7.9794 |  |  |  | -23.064 |  |  |  |  | -5.9488 |  | 350.63 |  | -29.68 | [6 empty] | 92.157 | 37.599 | 99.602 | -9.772 | 28.367 | -4.2196 | 52.103 | -3.9424 |  | 35.641 | -20.488 | -8.4502 | -11.397 | 39.754 | -37.38 | -15.954 | -72.015 | 47.268 | 154.15 | 37.562 | 13.755 | 63.42 | -9.8623 |  |  | 0
NIST/NRC 3 | 17.278 | [5 empty] | -3.4364 | [5 empty] | 1.0814 |  |  |  | -12.219 |  |  |  |  | -15.385 |  |  | 19.149 | 9.948 | -2.2124 | 6.2241 | -17.907 | 32.544 |  |  | 26.998 |  | 45.993 | -2.8868 | -8.6346 | -29.656 | 11.679 | 2.3806 |  | 63.176 | 18.023 | 74.914 | 31.181 | 166.79 | 17.498 | 24.893 | -31.383 | 38.188 | 23.183 | 37.691 | 11.204 | 81.963 | -14.538 | 18.387 | -43.252 | 0
NIST/NRC 9 | 18.06 | [5 empty] | -4.1096 | [5 empty] | 2.9476 |  |  |  | -14.058 |  |  |  |  | -21.982 |  |  | 19.828 | 7.8772 | -4.1758 | -0.63521 | -19.836 | 32.812 |  |  | 27.644 | -11.912 | 51.199 | -2.5983 | -4.2208 | -28.681 | 17.52 | 0.93499 |  | 62.976 | 12.528 | 68.309 | 39.535 | 161.85 | 10.837 | -6.1886 | -33.08 | 36.974 | 23.031 | 39.674 |  | 79.334 | -14.263 | -3.3559 | -42.678 | 0
NIST/NRC 5 | 12.607 | [5 empty] | -9.7796 | [5 empty] | -4.3787 |  |  |  | -7.9999 |  |  |  |  | -13.333 |  |  | 4.0982 | 8.2882 | 22.299 | 38.868 | -26.732 | 17.939 |  |  | 4.3414 | -25.376 | 19.39 | -26.417 | -27.486 | -40.422 | -27.946 | -23.008 |  | 55.816 | 8.8083 | 63.112 | 25.957 | 157.21 | -39.181 | 20.897 | -39.59 | 29.326 | 6.383 | 25.204 | 6.6353 | 77.735 | -75.927 | 16.115 | -39.024 | 0
NIST/NRC 14 | 16.514 | [5 empty] | -3.4364 | [5 empty] | 0.49848 |  |  |  | -15.838 |  |  |  |  | -23.636 |  |  | 52.246 | 4.0912 | 4.0201 | 16.657 | -15.304 | -2.927 |  |  | 95.545 |  | 73.955 | -34.104 | 51.337 | -1.8696 | 60.297 | -23.207 |  | 60.839 | -12.724 | 71.659 | 28.049 | 170.11 | 31.985 | 21.75 | -42.96 | 34.668 | -27.16 | 45.169 | 8.3066 | 84.666 | 13.426 | 13.816 | -37.747 | 0
NIST/NRC 15 | 15.128 | [5 empty] | -3.4602 | [5 empty] | -0.73828 |  |  |  | -14.423 |  |  |  |  | -17.647 |  |  | 12.904 | -5.3755 | -50.132 | -14.027 | -76.862 | 63.016 |  |  | -88.505 |  | -81.117 | 79.37 | -90.339 | -72.526 | -77.736 | 60.321 |  | -16.515 | -8.382 | 51.357 | 23.841 | 162.28 | 0.68666 | 21.656 | -35.214 | 24.856 | -37.337 | 23.896 | 0.19215 | 67.8 | -39.088 |  |  | 0
NIST/NRC 18 | 25.69 | [5 empty] | 3.4364 | [5 empty] | 3.5366 |  |  |  | -11.111 |  |  |  |  | -12 |  |  | 27.854 | 6.9658 | -3.6093 | 2.21 | -18.872 |  |  |  | 6.9759 |  | 5.5957 | 46.671 | -11.39 | -15.96 | -15.922 | 25.106 |  | 56.647 | -20.648 | 64.179 | 24.509 | 184.66 | 29.002 | 33.472 | -22.286 | 37.651 |  | 34.558 | 4.7959 | 95.622 | 10.542 | 19.518 |  | 0
iBMB Pool 1 | -11.765 | [5 empty] | 20.952 | [19 empty] | 7.4334 | 42.857 | 22.382 | [7 empty] | 49.117 | -14.568 | 24.698 |  |  | -4.4981 | -63.91 | [14 empty] | 0
iBMB Cable 4 | 17.099 | [5 empty] | -20.37 | [9 empty] | -9.3656 | [9 empty] | -14.384 | -15.695 | -15.48 | -16.457 | 64.589 | -14.286 |  |  |  |  | -47.645 |  | -97.172 |  | -52.521 | -29.004 | 500 | -55.109 | -44.679 | -54.088 | -45.556 | [10 empty] | 0
FM/SNL 4 | 16.845 | [11 empty] | 62.436 | 55.746 |  | 19.968 | [41 empty] | 0
FM/SNL 5 | 11.277 | [11 empty] | 43.427 | 42.694 |  | 19.911 | [41 empty] | 0
FM/SNL 21 | 33.282 | [11 empty] | 112.47 | 61.644 |  | 135.44 | [41 empty] | 0
FM/NBS 19 | 19.114 | 51.951 | 40.244 | 9.0789 | -17.095 | 20.287 | -27.759 | 15.436 | 15.379 | 18.963 | 21.937 | 17.28 |  |  |  |  | 9.7246 | -19.611 |  | -18.368 | -22.856 | 55.716 | -14.381 | [34 empty] | 0
FM/NBS 21 | -5.1039 | 23.672 | 11.557 | -11.117 | -20.627 | -19.202 | 33.036 | 14.355 | 16.5 | 18.991 | 16.082 | 15.14 |  |  |  |  | 31.991 | -6.5088 | -11.639 | -15.415 | -14.762 | 45.68 | 22.343 | [34 empty] | 0
NBS 100A | -8.467 | 2.2017 | 13.946 | 18.516 |  |  | 3.8318 | 1.3471 | -8.0806 | 0.48813 | [47 empty] | 0
NBS 100O | 7.5805 | -29.577 | -24.706 | [54 empty] | 0
NBS 100Z | -15.873 | -4.9253 | -5.1233 | -8.5186 |  |  | -1.464 | 29.477 | 25.197 | -47.707 | [47 empty] | 0
NBS F1 | -5.4458 | -18.728 |  |  |  |  | -5.0415 | -11.734 | [8 empty] | -68.141 | -66.646 |  |  |  | -33.442 | -28.779 | [34 empty] | 0
NBS F2 | 8.055 | -30.43 |  |  |  |  | -18.689 | 26.102 | [8 empty] | -62.77 | -51.333 |  |  |  | -28.053 | 1.9001 | [34 empty] | 0
NBS W1 | -24.148 | [5 empty] | -23.323 | [18 empty] | 154.82 | [31 empty] | 0
NBS W2 | 52.305 | [5 empty] | -22.044 | [18 empty] | 281.62 | [31 empty] | 0
NIST Plaza | 7.8258 | -8.5528 | 291.8 | [13 empty] | -28.89 |  |  |  |  | -24.034 | [35 empty] | 0
NIST HB 5 | [15 empty] | 24.8156
NIST HB 6 | [15 empty] | 24.4197
NIST HB 7 | [15 empty] | 11.2041
NIST HB 14 | [15 empty] | 12.4484
NIST HB 15 | [15 empty] | 12.3232
NIST HB 17 | [15 empty] | 9.6787
NIST HB 18 | [15 empty] | 14.6707
NIST HB 20 | [15 empty] | 7.4122
NIST HB 21 | [15 empty] | 4.2578

## HGT & HGL
[9 empty] | Absolute Values |  |  | Averages by Series
|  |  | Hot Gas Layer Temperature Rise |  |  | Hot Gas Layer Depth |  |  | HGL Temperature | HGL Depth |  | HGL Temperature | HGL Depth
Series | Test | Measurement Position | Exp | CFAST | Relative Difference | Exp | CFAST | Relative Difference | Relative Difference | Relative Difference | Series | Relative Difference | Relative Difference
|  |  | (°C) | (°C) | (%) | (m) | (m) | (%) | (%) | (%) |  | (%) | (%)
VTT | Case 1 |  | 54.8 | 62.3 | 13.686 |  |  |  | 13.686 |  | BE2 | 13.035 | 7.7922
| Case 2 |  | 86 | 99 | 15.116 |  |  |  | 15.116
| Case 3 |  | 82.5 | 91 | 10.303 | 13.86 | 14.94 | 7.7922 | 10.303 | 7.7922
NIST / NRC | Test 1 |  | 122.93 | 135.48 | 10.207 |  |  |  | 10.207 |  | BE3 | 12.0038 | 4.6098
| Test 7 |  | 116.8 | 133 | 13.87 |  |  |  | 13.87
| Test 2 |  | 229 | 234.57 | 2.4336 |  |  |  | 2.4336
| Test 8 |  | 218.2 | 234 | 7.2411 |  |  |  | 7.2411
| Test 4 |  | 204.2 | 222 | 8.7169 |  |  |  | 8.7169
| Test 10 |  | 198.3 | 221 | 11.447 |  |  |  | 11.447
| Test 13 |  | 290.24 | 311 | 7.1515 |  |  |  | 7.1515
| Test 16 |  | 268.46 | 290 | 8.0224 |  |  |  | 8.0224
| Test 17 |  | 135.3 | 143 | 5.6911 |  |  |  | 5.6911
| Test 3 |  | 207.2 | 243 | 17.278 | 2.91 | 2.81 | -3.4364 | 17.278 | 3.4364
| Test 9 |  | 204.13 | 241 | 18.06 | 2.92 | 2.8 | -4.1096 | 18.06 | 4.1096
| Test 5 |  | 175.83 | 198 | 12.607 | 2.9483 | 2.66 | -9.7796 | 12.607 | 9.7796
| Test 14 |  | 207.7 | 242 | 16.514 | 2.91 | 2.81 | -3.4364 | 16.514 | 3.4364
| Test 15 |  | 210.2 | 242 | 15.128 | 2.89 | 2.79 | -3.4602 | 15.128 | 3.4602
| Test 18 |  | 193.33 | 243 | 25.69 | 2.91 | -2.81 | 3.4364 | 25.69 | 3.4364
iBMB | Test 1 |  | 700.4 | 618 | -11.765 | 4.2 | 5.08 | 20.952 | 11.765 | 20.952 | BE4 | 11.765 | 20.952
iBMB | Test 4 |  | 150.3 | 176 | 17.099 | 4.32 | 3.44 | -20.37 | 17.099 | 20.37 | BE5 | 17.099 | 20.37
FM SNL | Test 4 |  | 59 | 68.938 | 16.845 |  |  |  | 16.845 |  | FM SNL | 20.468
| Test 5 |  | 44.223 | 49.21 | 11.277 |  |  |  | 11.277
| Test 21 |  | 66 | 87.966 | 33.282 |  |  |  | 33.282
FM NBS | FM 19 | Burn Room | 244.13 | 290.8 | 19.114 | 1.9615 | 1.417 | -27.759 | 19.114 | 27.759 | FM NBS | 20.7541 | 19.2382
|  | Corridor | 57.5 | 87.372 | 51.951 | 1.99 | 2.2972 | 15.436 | 51.951 | 15.436
|  | Corridor | 62.3 | 87.372 | 40.244 | 1.991 | 2.2972 | 15.379 | 40.244 | 15.379
|  | Corridor | 80.1 | 87.372 | 9.0789 | 1.931 | 2.2972 | 18.963 | 9.0789 | 18.963
|  | Target Room 1 | 52.3 | 43.359 | -17.095 | 1.9867 | 2.4225 | 21.937 | 17.095 | 21.937
|  | Target Room 2 | 44.145 | 20.287 | 20.287 | 2.05 | 2.4042 | 17.28 | 20.287 | 17.28
| FM 21 | Burn Room | 345.33 | 327.71 | -5.1039 | 1.719 | 2.2869 | 33.036 | 5.1039 | 33.036
|  | Corridor | 83.8 | 103.64 | 23.672 | 2.1088 | 2.4115 | 14.355 | 23.672 | 14.355
|  | Corridor | 92.9 | 103.64 | 11.557 | 2.07 | 2.4115 | 16.5 | 11.557 | 16.5
|  | Corridor | 116.6 | 103.64 | -11.117 | 2.0267 | 2.4115 | 18.991 | 11.117 | 18.991
|  | Target Room 1 | 75.2 | 59.688 | -20.627 | 2.11 | 2.4493 | 16.082 | 20.627 | 16.082
|  | Target Room 2 | 75.2 | 60.76 | -19.202 | 2.11 | 2.4294 | 15.14 | 19.202 | 15.14
NBS | MV100A | Burn Room | 259.39 | 237.43 | -8.467 | 1.27 | 1.3187 | 3.8318 | 8.467 | 3.8318 | NBS | 12.6759 | 14.6991
|  | Corridor 18 | 86.16 | 88.057 | 2.2017 | 1.17 | 1.1858 | 1.3471 | 2.2017 | 1.3471
|  | Corridor 38 | 77.28 | 88.057 | 13.946 | 1.29 | 1.1858 | -8.0806 | 13.946 | 8.0806
|  | Corridor Exit | 74.3 | 88.057 | 18.516 | 1.18 | 1.1858 | 0.48813 | 18.516 | 0.48813
| MV100O | Burn Room | 312 | 335.65 | 7.5805 |  |  |  | 7.5805
|  | Corridor 18 | 106.2 | 74.789 | -29.577 |  |  |  | 29.577
|  | Corridor 38 | 99.33 | 74.789 | -24.706 |  |  |  | 24.706
Corridor Exit
| MV100Z | Burn Room | 285.67 | 240.33 | -15.873 | 1.34 | 1.3204 | -1.464 | 15.873 | 1.464
|  | Corridor 18 | 67.08 | 63.776 | -4.9253 | 1.17 | 1.5149 | 29.477 | 4.9253 | 29.477
|  | Corridor 38 | 67.22 | 63.776 | -5.1233 | 1.21 | 1.5149 | 25.197 | 5.1233 | 25.197
|  | Target Room | 36.59 | 33.473 | -8.5186 | 1.41 | 2.0827 | -47.707 | 8.5186 | 47.707
| Test F1 | Burn Room | 769.85 | 727.93 | -5.4458 | 2.0714 | 1.967 | -5.0415 | 5.4458 | 5.0415 |  | 15.6647 | 15.3916
|  |  | 895.67 | 727.93 | -18.728 | 2.2285 | 1.967 | -11.734 | 18.728 | 11.734
| Test F6 | Burn Room | 563.92 | 609.34 | 8.055 | 2.2335 | 1.8161 | -18.689 | 8.055 | 18.689
|  |  | 875.87 | 609.34 | -30.43 | 1.4402 | 1.8161 | 26.102 | 30.43 | 26.102
| Test W1 | Burn Room | 777 | 589.37 | -24.148 | 2.2312 | 1.7108 | -23.323 | 24.148 | 23.323 |  | 38.2265 | 22.6835
| Test W2 | Burn Room | 783.38 | 1193.1 | 52.305 | 2.3297 | 1.8162 | -22.044 | 52.305 | 22.044
NIST Plaza | Test 7 | Burn Room | 154.54 | 166.63 | 7.8258 |  |  |  | 7.8258 |  | NIST Plaza | 8.1893
|  | Corridor | 424.02 | 387.76 | -8.5528 |  |  |  | 8.5528
|  | Floor 7 | 0.582 | 2.2803 | 291.8 |  |  |  | 291.8
Average ----> |  |  |  |  | 5.8258 |  |  | 3.1797 | 15.8038 | 15.2045
Standard Deviation ----> |  |  |  |  | 18.3043 |  |  | 18.4799 | 10.7311 | 10.6742
Median ----> |  |  |  |  | 8.7169 |  |  | 3.4364 | 13.87 | 15.436
Percentile ranking at uncertainty limit ----> | [8 empty] | 0.519 | 0.396
90th percentile value (90 % of predictions are within xxx %) ----> | [8 empty] | 30.0888 | 27.0962

## Plume Temp
[6 empty] | Absolute Values |  | Averages by Series
|  |  | Plume Temperature Rise |  |  | Plume Temperature |  | HGL Temperature
Series | Test | Measurement Position | Exp | CFAST | Relative Difference | Relative Difference | Series | Relative Difference
|  |  | (°C) | (°C) | (%) | (%) |  | (%)
VTT | Case 1 | T G.1 | 166 | 174 | 4.8193 | 4.8193 | VTT | 16.3256
|  | T G.2 | 77 | 105 | 36.364 | 36.364
| Case 2 | T G.1 | 288 | 244 | -15.278 | 15.278
|  | T G.2 | 128 | 161 | 25.781 | 25.781
| Case 3 | T G.1 | 252 | 238 | -5.5556 | 5.5556
|  | T G.2 | 128 | 141 | 10.156 | 10.156
FM SNL | Test 4 | Ch 28 | 114.2 | 137 | 19.968 | 19.968 | FM SNL | 19.9395
| Test 5 | Ch 28 | 93.402 | 112 | 19.911 | 19.911
| Test 21 | Ch 6 | 79 | 186 | 135.44
NIST High Bay | Test 5 | 22 m | 32 | 42.562 | 24.8156 | 24.8156 | NIST High Bay | 13.47
| Test 6 | 22 m | 29 | 38.3698 | 24.4197 | 24.4197
| Test 7 | 22 m | 46 | 51.8042 | 11.2041 | 11.2041
| Test 14 | 22 m | 79 | 90.2325 | 12.4484 | 12.4484
| Test 15 | 22 m | 127 | 144.8501 | 12.3232 | 12.3232
| Test 17 | 22 m | 119 | 131.7518 | 9.6787 | 9.6787
| Test 18 | 22 m | 55 | 64.4562 | 14.6707 | 14.6707
| Test 20 | 22 m | 130 | 140.4073 | 7.4122 | 7.4122
| Test 21 | 22 m | 234 | 244.4064 | 4.2578 | 4.2578
Average ----> |  |  |  |  | 12.788 | 15.239
Standard Deviation ----> |  |  |  |  | 12.2964 | 8.8438
Median ----> |  |  |  |  | 12.3232 | 12.4484
Percentile ranking at uncertainty limit ----> | [5 empty] | 0.543
90th percentile value (90 % of predictions are within xxx %) ----> | [5 empty] | 25.2017

## Ceiling Jet
Comparison of ceiling jet temperature with upper gas layer temperature
|  |  | Ceiling Jet Temperature Rise |  |  | Absolute Values
Series | Test | Measurement Position | Exp | CFAST | Relative Difference | Relative Difference | Series | Test | Measurement Position | Ceiling Jet | HGT | Difference
|  |  | (°C) | (°C) | (%) | (%) |  |  |  | (°C) | (°C) | (°C)
NIST / NRC | Test 1 |  | 154.57 | 135.48 | -12.348 | 12.348 | BE3 | Test 1 |  | 154.57 | 122.93 | 31.64
| Test 7 |  | 139.07 | 133 | -4.3625 | 4.3625 |  | Test 7 |  | 139.07 | 116.8 | 22.27
| Test 2 |  | 270.46 | 234.57 | -13.27 | 13.27 |  | Test 2 |  | 270.46 | 229 | 41.46
| Test 8 |  | 247.24 | 234 | -5.3556 | 5.3556 |  | Test 8 |  | 247.24 | 218.2 | 29.04
| Test 4 |  | 227.7 | 222 | -2.5033 | 2.5033 |  | Test 4 |  | 227.7 | 204.2 | 23.5
| Test 10 |  | 217 | 221 | 1.8434 | 1.8434 |  | Test 10 |  | 217 | 198.3 | 18.7
| Test 13 |  | 330.05 | 311 | -5.7716 | 5.7716 |  | Test 13 |  | 330.05 | 290.24 | 39.81
| Test 16 |  | 277.3 | 290 | 4.5799 | 4.5799 |  | Test 16 |  | 277.3 | 268.46 | 8.84
| Test 17 |  | 155.4 | 143 | -7.9794 | 7.9794 |  | Test 17 |  | 155.4 | 135.3 | 20.1
| Test 3 |  | 240.4 | 243 | 1.0814 | 1.0814 |  | Test 3 |  | 240.4 | 207.2 | 33.2
| Test 9 |  | 234.1 | 241 | 2.9476 | 2.9476 |  | Test 9 |  | 234.1 | 204.13 | 29.97
| Test 5 |  | 207.07 | 198 | -4.3787 | 4.3787 |  | Test 5 |  | 207.07 | 175.83 | 31.24
| Test 14 |  | 240.8 | 242 | 0.49848 | 0.49848 |  | Test 14 |  | 240.8 | 207.7 | 33.1
| Test 15 |  | 243.8 | 242 | -0.73828 | 0.73828 |  | Test 15 |  | 243.8 | 210.2 | 33.6
| Test 18 |  | 234.7 | 243 | 3.5366 | 3.5366 |  | Test 18 |  | 234.7 | 193.33 | 41.37
FM SNL | Test 4 | Sec 1 | 82.18 | 133.49 | 62.436 | 62.436 | FM SNL | Test 4 | Sec 1 | 82.18 | 59 | 23.18
|  | Sec 3 | 65.78 | 102.45 | 55.746 | 55.746 |  |  | Sec 3 | 65.78 | 59 | 6.78
| Test 5 | Sec 1 | 70.419 | 101 | 43.427 | 43.427 |  | Test 5 | Sec 1 | 70.419 | 44.223 | 26.196
|  | Sec 3 | 52.56 | 75 | 42.694 | 42.694 |  |  | Sec 3 | 52.56 | 44.223 | 8.337
| Test 21 | Sec 1 | 74.833 | 159 | 112.47 | 112.47 |  | Test 21 | Sec 1 | 74.833 | 66 | 8.833
|  | Sec 3 | 76.9 | 124.3 | 61.644 | 61.644 |  |  | Sec 3 | 76.9 | 66 | 10.9
Average ----> |  |  |  |  | 16.0094 | 21.4101
Standard Deviation ----> |  |  |  |  | 33.4125 | 30.07
Median ----> | [5 empty] | 5.3556
Percentile ranking at uncertainty limit ----> | [5 empty] | 0.704
90th percentile value (90 % of predictions are within xxx %) ----> | [5 empty] | 61.644
90th percentile not counting FM tests ----> | [5 empty] | 10.6006

## Gas Concentration
[9 empty] | Absolute Value |  | Average by Test Series
|  |  | HGL Oxygen Concentration Decrease |  |  | HGL Carbon Dioxide Concentration |  |  | O2 | CO2
Series | Test | Measurement Position | Exp | CFAST | Relative Difference | Exp | CFAST | Relative Difference | Relative Difference | Relative Difference
|  |  | (molar fraction) | (molar fraction) | (%) | (molar fraction) | (molar fraction) | (%) | (%) | (%)
NIST / NRC | Test 1 |  | 0.065 | 0.076111 | 17.094 | 0.0384 | 0.044428 | 15.697 | 17.094 | 15.697 | 15.0331 | 14.2738
| Test 7 |  | 0.064 | 0.073 | 14.062 | 0.037983 | 0.0426 | 12.154 | 14.062 | 12.154
| Test 2 |  | 0.092333 | 0.10048 | 8.8264 | 0.05455 | 0.058654 | 7.5225 | 8.8264 | 7.5225
| Test 8 |  | 0.095833 | 0.098 | 2.2609 | 0.057817 | 0.0574 | -0.72067 | 2.2609 | 0.72067
| Test 4 |  | 0.078 | 0.06 | -23.077 | 0.04735 | 0.035 | -26.082 | 23.077 | 26.082
| Test 10 |  | 0.078833 | 0.06 | -23.89 | 0.046433 | 0.0347 | -25.269 | 23.89 | 25.269
| Test 13 |  | 0.1008 | 0.1097 | 8.8252 | 0.059988 | 0.0644 | 7.3545 | 8.8252 | 7.3545
| Test 16 |  | 0.090941 | 0.075 | -17.529 | 0.05518 | 0.043817 | -20.594 | 17.529 | 20.594
| Test 17 |  | 0.032961 | 0.031 | -5.9488 | 0.021576 | 0.0166 | -23.064 | 5.9488 | 23.064
| Test 3 |  | 0.052 | 0.044 | -15.385 | 0.0311 | 0.0273 | -12.219 | 15.385 | 12.219
| Test 9 |  | 0.053833 | 0.042 | -21.982 | 0.0313 | 0.0269 | -14.058 | 21.982 | 14.058
| Test 5 |  | 0.03 | 0.026 | -13.333 | 0.0175 | 0.0161 | -7.9999 | 13.333 | 7.9999
| Test 14 |  | 0.055 | 0.042 | -23.636 | 0.0322 | 0.0271 | -15.838 | 23.636 | 15.838
| Test 15 |  | 0.051 | 0.042 | -17.647 | 0.0312 | 0.0267 | -14.423 | 17.647 | 14.423
| Test 18 |  | 0.05 | 0.044 | -12 | 0.0306 | 0.0272 | -11.111 | 12 | 11.111
iBMB | Test 4 |  | 0.023833 | 0.02 | -16.084 | 0.012909 | 0.0117 | -9.3656 | 16.084 | 9.3656 | 16.084 | 9.3656
FM NBS | FM19 | Burn Room | 0.031 | 0.048272 | 55.716 | 0.022917 | 0.025145 | 9.7246 | 55.716 | 9.7246 | 34.53 | 16.7639
|  | Corridor | 0.037 | 0.031679 | -14.381 | 0.0205 | 0.01648 | -19.611 | 14.381 | 19.611
|  | Target Room 1 |  |  |  | 0.0182 | 0.014857 | -18.368 |  | 18.368
|  | Target Room 2 |  |  |  | 0.0194 | 0.014966 | -22.856 |  | 22.856
| FM21 | Burn Room | 0.06 | 0.087408 | 45.68 | 0.0341 | 0.045009 | 31.991 | 45.68 | 31.991
|  | Corridor | 0.046 | 0.056278 | 22.343 | 0.031 | 0.028982 | -6.5088 | 22.343 | 6.5088
|  | Corridor |  |  |  | 0.0328 | 0.028982 | -11.639 |  | 11.639
|  | Target Room 1 |  |  |  | 0.0287 | 0.024276 | -15.415 |  | 15.415
|  | Target Room 2 |  |  |  | 0.0288 | 0.024549 | -14.762 |  | 14.762
NBS | Test F1 | Burn Room | 0.209 | 0.13911 | -33.442 | 0.16911 | 0.053877 | -68.141 | 33.442 | 68.141 | 23.0435 | 62.2225
|  |  | 0.19532 | 0.13911 | -28.779 | 0.16153 | 0.053877 | -66.646 | 28.779 | 66.646
| Test F6 | Burn Room | 0.14029 | 0.10093 | -28.053 | 0.10602 | 0.039471 | -62.77 | 28.053 | 62.77
|  |  | 0.09905 | 0.10093 | 1.9001 | 0.081104 | 0.039471 | -51.333 | 1.9001 | 51.333
NIST Plaza |  |  | 0.1103 | 0.083791 | -24.034 | 0.0403 | 0.028657 | -28.89 | 24.034 | 28.89 | 24.034 | 28.89
Average ----> |  |  |  |  | -4.9358 |  |  | -15.6673 | 19.6614 | 21.491
Standard Deviation ----> | [8 empty] | 12.3187 | 17.7879
Median ----> | [8 empty] | 17.529 | 15.556
Percentile ranking at uncertainty limit ----> | [8 empty] | 0.168 | 0.163
90th percentile value (90 % of predictions are within xxx %) ----> | [8 empty] | 31.5768 | 52.4767

## Smoke Concentration
Smoke Concentration
Series | Test | Exp | CFAST | Relative Difference
|  | (mg/m3) | (mg/m3) | (%)
NIST / NRC | Test 1 | 41.467 | 320.45 | 672.79
| Test 7 | 55.05 | 307 | 457.67
| Test 2 | 128 | 419.47 | 227.71
| Test 8 | 99.5 | 411 | 313.07
| Test 4 | 79.892 | 177 | 121.55
| Test 10 | 70.684 | 177 | 150.41
| Test 13 | 223.73 | 480 | 114.55
| Test 16 | 139 | 205 | 47.482
| Test 17 | 352.84 | 1590 | 350.63
| Test 3 | 117.5 | 140 | 19.149
| Test 9 | 116 | 139 | 19.828
| Test 5 | 87.033 | 90.6 | 4.0982
| Test 14 | 91.3 | 139 | 52.246
| Test 15 | 124 | 140 | 12.904
| Test 18 | 109.5 | 140 | 27.854
Average ----> |  |  |  | 172.7961
| Closed door tests ----> |  |  | 272.8736
| Open door tests ----> |  |  | 22.6799
Median ----> |  |  |  | 114.55
227.71
19.4885
Percentile ranking closed door tests ---> |  |  |  | 0
Percentile ranking open door tests ---> |  |  |  | 0.817
90th percentile value closed door tests |  |  |  | 500.694
90th percentile value open door tests |  |  |  | 40.05

## Pressure
Comparment Pressure Rise
Series | Test | Exp | CFAST | Relative Difference
|  | (Pa) | (Pa) | (%)
NIST / NRC | Test 1 | 57.522 | 42.398 | -26.292 | 26.292
| Test 7 | 45.882 | 28.8 | -37.231 | 37.231
| Test 2 | 290 | 266.05 | -8.2593 | 8.2593
| Test 8 | 189 | 214 | 13.227 | 13.227
| Test 4 | 56.6 | 76.8 | 35.689 | 35.689
| Test 10 | 49.267 | 45.7 | -7.2395 | 7.2395
| Test 13 | 232 | 336 | 44.828 | 44.828
| Test 16 | 80.529 | 225 | 179.4 | 179.4
| Test 17 | 194.82 | 137 | -29.68 | 29.68
| Test 3 | -1.91 | -2.1 | 9.948 | 9.948
| Test 9 | -1.9467 | -2.1 | 7.8772 | 7.8772
| Test 5 | -1.81 | -1.96 | 8.2882 | 8.2882
| Test 14 | -2.0367 | -2.12 | 4.0912 | 4.0912
| Test 15 | -2.325 | -2.2 | -5.3755 | 5.3755
| Test 18 | -2.01 | -2.15 | 6.9658 | 6.9658
NBS | Test W1 | -1.8401 | -4.689 | 154.82 | 154.82
| Test W2 | -1.716 | -6.5486 | 281.62 | 281.62
Average ----> |  |  |  | 37.2163 | 50.6372
Standard Deviation ----> |  |  |  | 86.1607 | 78.5551
Median ----> |  |  |  |  | 13.227
Percentile ranking at uncertainty limit ----> |  |  |  |  | 0.772
90th percentile value ----> |  |  |  |  | 164.652
90th percentile value not counting NBS ----> |  |  |  |  | 41.7892

## Target Flux and Temperature
|  |  | Radiant Heat Flux to Targets |  |  | Total Heat Flux to Targets |  |  | Target Temperature Rise |  |  | Rad Flux | Total Flux | Temp
| Test | Position | Exp | CFAST | Diff | Exp | CFAST | Diff | Exp | CFAST | Diff | Diff
|  |  | (kW/m2) | (kW/m2) | (%) | (kW/m2) | (kW/m2) | (%) | (°C) | (°C) | (%) | (%)
NIST / NRC | Test 1 | B | 1.1198 | 2.32 | 107.18 | 1.8446 | 2.46 | 33.359 | 106.4 | 102.77 | -3.4107 | 107.18 | 33.359 | 3.4107
|  | D | 1.4394 | 1.5 | 4.2131 | [6 empty] | 4.2131
|  | F | 0.86659 | 1.36 | 56.938 | 1.5926 | 2.37 | 48.81 | 82.6 | 67.853 | -17.854 | 56.938 | 48.81 | 17.854
|  | G33 | 1.5094 | 1.51 | 0.040232 |  |  |  | 64.317 | 95.955 | 49.191 | 0.040232 |  | 49.191
| Test 7 | B | 1.2072 | 2.27 | 88.031 | 1.8421 | 2.4 | 30.284 | 109.5 | 102 | -6.8493 | 88.031 | 30.284 | 6.8493
|  | D | 1.3491 | 1.47 | 8.9608 | 2.5188 | 2.4467 | -2.8634 | 87.7 | 102 | 16.306 | 8.9608 | 2.8634 | 16.306
|  | F | 0.81985 | 1.33 | 62.224 | 1.5004 | 2.31 | 53.961 | 90.1 | 73.3 | -18.646 | 62.224 | 53.961 | 18.646
|  | G33 | 1.4664 | 1.48 | 0.92903 | 1.8913 | 2.21 | 16.851 | 77.9 | 93 | 19.384 | 0.92903 | 16.851 | 19.384
| Test 2 | B | 2.8818 | 5.37 | 86.34 | 5.2517 | 5.77 | 9.8698 | 175.37 | 143.98 | -17.898 | 86.34 | 9.8698 | 17.898
|  | D | 4.0262 | 4.12 | 2.3294 | 9.3142 | 5.91 | -36.548 | 124.3 | 145.47 | 17.033 | 2.3294 | 36.548 | 17.033
|  | F | 1.9867 | 3.71 | 86.741 | 4.6796 | 5.51 | 17.745 | 128.57 | 112.25 | -12.69 | 86.741 | 17.745 | 12.69
|  | G33 | 5.9673 | 4.12 | -30.957 |  |  |  | 106.6 | 138.22 | 29.665 | 30.957 |  | 29.665
| Test 8 | B | 2.9151 | 5.33 | 82.84 | 5.5811 | 5.73 | 2.6679 | 183.1 | 142 | -22.447 | 82.84 | 2.6679 | 22.447
|  | D | 3.5563 | 4.07 | 14.446 | 8.4749 | 5.87 | -30.736 | 149.6 | 143 | -4.4118 | 14.446 | 30.736 | 4.4118
|  | F | 1.9294 | 3.66 | 89.7 | 4.907 | 5.46 | 11.27 | 131.3 | 111 | -15.461 | 89.7 | 11.27 | 15.461
|  | G33 | 6.0171 | 4.08 | -32.193 | 5.9798 | 5.44 | -9.0277 | 106.4 | 136 | 27.82 | 32.193 | 9.0277 | 27.82
| Test 4 | B | 2.909 | 4.96 | 70.504 | 5.5228 | 5.36 | -2.9476 | 147.97 | 156 | 5.429 | 70.504 | 2.9476 | 5.429
|  | D | 3.2523 | 3.8 | 16.84 | 7.232 | 5.49 | -24.087 | 112.63 | 157 | 39.39 | 16.84 | 24.087 | 39.39
|  | F | 2.0209 | 3.43 | 69.724 | 5.0203 | 5.12 | 1.9861 | 147.93 | 115 | -22.262 | 69.724 | 1.9861 | 22.262
|  | G33 | 5.9979 | 3.79 | -36.811 | 6.3937 | 5.07 | -20.703 | 124.53 | 149 | 19.647 | 36.811 | 20.703 | 19.647
| Test 10 | B | 2.6752 | 4.9267 | 84.158 | 4.8356 | 5.33 | 10.223 | 143.5 | 161.67 | 12.66 | 84.158 | 10.223 | 12.66
|  | D | 2.9163 | 3.77 | 29.271 | 6.6501 | 5.46 | -17.896 | 131.87 | 163 | 23.61 | 29.271 | 17.896 | 23.61
|  | F | 1.9192 | 3.4 | 77.158 | 4.3199 | 5.09 | 17.826 | 150 | 128 | -14.667 | 77.158 | 17.826 | 14.667
|  | G33 | 5.4231 | 3.76 | -30.666 | 6.201 | 5.03 | -18.884 | 147.97 | 149 | 0.6984 | 30.666 | 18.884 | 0.6984
| Test 13 | B | 4.7675 | 8.88 | 86.26 | 8.2506 | 9.67 | 17.204 | 185.46 | 165 | -11.032 | 86.26 | 17.204 | 11.032
|  | D | 6.5743 | 7.58 | 15.297 | 11.258 | 9.95 | -11.621 | 173.5 | 168 | -3.17 | 15.297 | 11.621 | 3.17
|  | F | 2.9006 | 6.79 | 134.09 | 7.2733 | 9.15 | 25.803 | 143.38 | 143 | -0.26536 | 134.09 | 25.803 | 0.26536
|  | G33 | 10.1 | 7.6 | -24.754 | 12.086 | 9.38 | -22.387 | 132.9 | 164 | 23.401 | 24.754 | 22.387 | 23.401
| Test 16 | B | 4.1078 | 7.6717 | 86.76 | 8.3467 | 8.4517 | 1.2574 | 160.1 | 166 | 3.6852 | 86.76 | 1.2574 | 3.6852
|  | D | 4.8232 | 6.4717 | 34.178 | 11.686 | 8.7017 | -25.537 | 155.11 | 170 | 9.5999 | 34.178 | 25.537 | 9.5999
|  | F | 2.7569 | 5.7417 | 108.26 | 6.139 | 7.9717 | 29.853 | 168.2 | 148 | -12.01 | 108.26 | 29.853 | 12.01
|  | G33 | 11.975 | 6.4517 | -46.124 | 12.177 | 8.1417 | -33.141 | 169.46 | 150.17 | -11.386 | 46.124 | 33.141 | 11.386
| Test 17 | B | 1.301 | 2.5 | 92.157 | 2.3604 | 3.03 | 28.367 |  |  |  | 92.157 | 28.367
|  | D | 1.5189 | 2.09 | 37.599 | 3.2783 | 3.14 | -4.2196 |  |  |  | 37.599 | 4.2196
|  | F | 0.88175 | 1.76 | 99.602 | 1.854 | 2.82 | 52.103 |  |  |  | 99.602 | 52.103
|  | G33 | 2.4161 | 2.18 | -9.772 | 3.0607 | 2.94 | -3.9424 |  |  |  | 9.772 | 3.9424
| Test 3 | B | 4.441 | 5.64 | 26.998 | 7.0924 | 6.48 | -8.6346 | 226 | 221 | -2.2124 | 26.998 | 8.6346 | 2.2124
|  | D |  |  |  | 9.4535 | 6.65 | -29.656 | 209.93 | 223 | 6.2241 |  | 29.656 | 6.2241
|  | F | 2.9453 | 4.3 | 45.993 | 5.5069 | 6.15 | 11.679 | 194.9 | 160 | -17.907 | 45.993 | 11.679 | 17.907
|  | G33 | 5.3546 | 5.2 | -2.8868 | 6.4465 | 6.6 | 2.3806 | 169 | 224 | 32.544 | 2.8868 | 2.3806 | 32.544
| Test 9 | B | 4.2854 | 5.47 | 27.644 | 6.5776 | 6.3 | -4.2208 | 227.5 | 218 | -4.1758 | 27.644 | 4.2208 | 4.1758
|  | D | 5.2448 | 4.62 | -11.912 | 9.0579 | 6.46 | -28.681 | 220.4 | 219 | -0.63521 | 11.912 | 28.681 | 0.63521
|  | F | 2.7315 | 4.13 | 51.199 | 5.08 | 5.97 | 17.52 | 194.6 | 156 | -19.836 | 51.199 | 17.52 | 19.836
|  | G33 | 5.1539 | 5.02 | -2.5983 | 6.3506 | 6.41 | 0.93499 | 166.4 | 221 | 32.812 | 2.5983 | 0.93499 | 32.812
| Test 5 | B | 3.8815 | 4.05 | 4.3414 | 6.7987 | 4.93 | -27.486 | 149.63 | 183 | 22.299 | 4.3414 | 27.486 | 22.299
|  | D | 4.7706 | 3.56 | -25.376 | 8.493 | 5.06 | -40.422 | 132.5 | 184 | 38.868 | 25.376 | 40.422 | 38.868
|  | F | 2.6384 | 3.15 | 19.39 | 6.4535 | 4.65 | -27.946 | 174.7 | 128 | -26.732 | 19.39 | 27.946 | 26.732
|  | G33 | 5.4496 | 4.01 | -26.417 | 6.689 | 5.15 | -23.008 | 161.1 | 190 | 17.939 | 26.417 | 23.008 | 17.939
| Test 14 | B | 2.8331 | 5.54 | 95.545 | 3.8193 | 5.78 | 51.337 | 199 | 207 | 4.0201 | 95.545 | 51.337 | 4.0201
|  | D |  |  |  | 6.0532 | 5.94 | -1.8696 | 178.3 | 208 | 16.657 |  | 1.8696 | 16.657
|  | F | 2.1155 | 3.68 | 73.955 | 3.4436 | 5.52 | 60.297 | 171.2 | 145 | -15.304 | 73.955 | 60.297 | 15.304
|  | G33 | 10.501 | 6.92 | -34.104 | 10.834 | 8.32 | -23.207 | 269.9 | 262 | -2.927 | 34.104 | 23.207 | 2.927
| Test 15 | B | 46.395 | 5.3333 | -88.505 | 57.758 | 5.58 | -90.339 | 415.1 | 207 | -50.132 | 88.505 | 90.339 | 50.132
|  | D |  |  |  | 20.893 | 5.74 | -72.526 | 243.1 | 209 | -14.027 |  | 72.526 | 14.027
|  | F | 18.165 | 3.43 | -81.117 | 23.94 | 5.33 | -77.736 | 669.9 | 155 | -76.862 | 81.117 | 77.736 | 76.862
|  | G33 | 3.7353 | 6.7 | 79.37 | 5.0773 | 8.14 | 60.321 | 161.33 | 263 | 63.016 | 79.37 | 60.321 | 63.016
| Test 18 | B | 5.2068 | 5.57 | 6.9759 | 7.5725 | 6.71 | -11.39 | 235.5 | 227 | -3.6093 | 6.9759 | 11.39 | 3.6093
|  | D |  |  |  | 7.8059 | 6.56 | -15.96 | 217.2 | 222 | 2.21 |  | 15.96 | 2.21
|  | F | 5.1423 | 5.43 | 5.5957 | 8.6705 | 7.29 | -15.922 | 231.73 | 188 | -18.872 | 5.5957 | 15.922 | 18.872
|  | G33 | 2.8431 | 4.17 | 46.671 | 4.4522 | 5.57 | 25.106 |  |  |  | 46.671 | 25.106
iBMB Pool | Test 1 | WS 2 |  |  |  | 27.16 | 40.5 | 49.117 | 356.5 | 383 | 7.4334 |  | 49.117 | 7.4334
|  | WS 3 |  |  |  | 48.576 | 41.5 | -14.568 | 308.7 | 441 | 42.857 |  | 14.568 | 42.857
|  | WS 4 |  |  |  | 32.398 | 40.4 | 24.698 | 490.27 | 600 | 22.382 |  | 24.698 | 22.382
iBMB Cable | Test 4 | WS 2 / TCO 1-3 |  |  |  | 3.61 | 1.89 | -47.645 | 87.6 | 75 | -14.384 |  | 47.645 | 14.384
|  | TCO 2-3 | [6 empty] | 111.5 | 94 | -15.695 |  |  | 15.695
|  | WS 3 / TCO 1-5 |  |  |  | 96.9 | 2.74 | -97.172 | 110.03 | 93 | -15.48 |  | 97.172 | 15.48
|  | TCO 2-5 | [6 empty] | 146.03 | 122 | -16.457 |  |  | 16.457
|  | WS 4 / TCO 1-7 |  |  |  | 5.7499 | 2.73 | -52.521 | 106.93 | 176 | 64.589 |  | 52.521 | 64.589
|  | TCO 2-7 | [6 empty] | 140 | 120 | -14.286 |  |  | 14.286
Average ----> |  |  |  |  | 30.9331 |  |  | -4.1686 |  |  | 2.3393 | 48.2257 | 26.7981 | 18.974
Standard Deviation ----> |  |  |  |  | 51.6728 |  |  | 34.5894 |  |  | 24.8453 | 35.7258 | 22.0082 | 16.0321
Median ----> |  |  |  |  | 27.321 |  |  | -3.9424 |  |  | -2.2124 | 37.205 | 23.008 | 16.306
Percentile ranking at uncertainty limit ----> | [11 empty] | 0.274 | 0.461 | 0.37
90th percentile value ----> | [11 empty] | 90.9285 | 53.673 | 39.2856

## Surface Flux and Temperature
Absolute Values
|  |  | Total Flux to Surface |  |  | Surface Temperature |  |  | Flux | Temp
Series | Test | Measurement Position | Exp | CFAST | Relative Difference | Exp | CFAST | Relative Difference | Relative Difference | Relative Difference
|  |  | (kW/m2) | (kW/m2) | (%) | (°C) | (°C) | (%) | (%) | (%)
NIST / NRC | Test 1 | Long Wall | 1.3844 | 1.96 | 41.578 | 54.183 | 88.943 | 64.152 | 41.578 | 64.152
|  |  | 1.7656 | 1.95 | 10.442 | 67.967 | 88.993 | 30.936 | 10.442 | 30.936
|  | Short Wall | 1.255 | 1.96 | 56.169 | 55.317 | 88.512 | 60.009 | 56.169 | 60.009
|  |  | 1.7178 | 1.96 | 14.1 | 70.95 | 89.118 | 25.607 | 14.1 | 25.607
|  | Floor | 0.9244 | 1.68 | 81.74 | 38.2 | 70.94 | 85.708 | 81.74 | 85.708
|  |  | 2.3877 | 1.65 | -30.896 | 77.383 | 69.215 | -10.556 | 30.896 | 10.556
|  | Ceiling | 1.9244 | 2.21 | 14.841 | 80.7 | 91.93 | 13.916 | 14.841 | 13.916
|  |  | 3.7535 | 2.17 | -42.188 | 176.13 | 90.611 | -48.555 | 42.188 | 48.555
| Test 7 | Long Wall | 1.3747 | 1.92 | 39.663 | 53.1 | 87 | 63.842 | 39.663 | 63.842
|  |  | 1.8779 | 1.9 | 1.1783 | 70.283 | 87 | 23.785 | 1.1783 | 23.785
|  | Short Wall | 1.2252 | 1.92 | 56.709 | 54.567 | 86 | 57.605 | 56.709 | 57.605
|  |  | 1.785 | 1.92 | 7.563 | 70.183 | 87 | 23.961 | 7.563 | 23.961
|  | Floor | 0.9018 | 1.64 | 81.859 | 36.3 | 68.6 | 88.981 | 81.859 | 88.981
|  |  | 2.3174 | 1.6 | -30.959 | 78.167 | 66.9 | -14.414 | 30.959 | 14.414
|  | Ceiling | 1.9419 | 2.15 | 10.719 | 80.4 | 89.333 | 11.111 | 10.719 | 11.111
[6 empty] | 191.3 | 88 | -53.999 |  | 53.999
| Test 2 | Long Wall | 3.7791 | 4.65 | 23.045 | 95.433 | 150.35 | 57.546 | 23.045 | 57.546
|  |  | 4.5046 | 4.61 | 2.3391 | 120.1 | 151.35 | 26.02 | 2.3391 | 26.02
|  | Short Wall | 3.5887 | 4.64 | 29.295 | 109.43 | 149.77 | 36.862 | 29.295 | 36.862
|  |  | 4.6104 | 4.64 | 0.64202 | 125.4 | 150.61 | 20.106 | 0.64202 | 20.106
|  | Floor | 2.5789 | 4.17 | 61.697 | 74.083 | 127.01 | 71.445 | 61.697 | 71.445
|  |  | 8.8987 | 4.06 | -54.376 | 156.2 | 123.54 | -20.911 | 54.376 | 20.911
|  | Ceiling | 5.6479 | 5.08 | -10.055 | 147.8 | 154.15 | 4.2977 | 10.055 | 4.2977
|  |  | 14.479 | 4.97 | -65.673 | 307.89 | 152.02 | -50.625 | 65.673 | 50.625
| Test 8 | Long Wall | 3.8412 | 4.61 | 20.015 | 95.1 | 149 | 56.677 | 20.015 | 56.677
|  |  | 3.211 | 4.57 | 42.325 | 131.87 | 150 | 13.751 | 42.325 | 13.751
|  | Short Wall | 2.464 | 4.6067 | 86.959 | 108.6 | 148 | 36.28 | 86.959 | 36.28
|  |  | 4.702 | 4.6 | -2.17 | 124.67 | 149 | 19.519 | 2.17 | 19.519
|  | Floor | 2.5541 | 4.12 | 61.309 | 71.2 | 125 | 75.562 | 61.309 | 75.562
|  |  | 8.6308 | 4.01 | -53.538 | 148.2 | 121 | -18.354 | 53.538 | 18.354
|  | Ceiling | 6.13 | 5.0467 | -17.673 | 147.23 | 152.67 | 3.6903 | 17.673 | 3.6903
|  |  | 12.958 | 4.9367 | -61.903 | 325.1 | 150.67 | -53.655 | 61.903 | 53.655
| Test 4 | Long Wall | 3.4053 | 4.25 | 24.807 | 97.133 | 150 | 54.427 | 24.807 | 54.427
|  |  | 3.5061 | 4.26 | 21.503 | 145.3 | 152 | 4.6112 | 21.503 | 4.6112
|  | Short Wall | 3.256 | 4.25 | 30.529 | 105.8 | 149 | 40.832 | 30.529 | 40.832
|  |  | 3.9791 | 4.25 | 6.8082 | 120.6 | 150 | 24.378 | 6.8082 | 24.378
|  | Floor | 2.4679 | 3.89 | 57.622 | 76.283 | 130 | 70.417 | 57.622 | 70.417
|  |  | 8.5064 | 3.8 | -55.328 | 151.6 | 127 | -16.227 | 55.328 | 16.227
|  | Ceiling | 5.0427 | 4.66 | -7.5893 | 147.17 | 153 | 3.9637 | 7.5893 | 3.9637
|  |  | 6.0174 | 4.63 | -23.057 | 180.1 | 153 | -15.047 | 23.057 | 15.047
| Test 10 | Long Wall | 3.3386 | 4.23 | 26.701 | 94.1 | 150 | 59.405 | 26.701 | 59.405
|  |  | 3.4799 | 4.23 | 21.554 | 161.7 | 151 | -6.6173 | 21.554 | 6.6173
|  | Short Wall | 3.1048 | 4.2267 | 36.135 | 106 | 149 | 40.566 | 36.135 | 40.566
|  |  | 3.875 | 4.22 | 8.9041 | 116.9 | 150 | 28.315 | 8.9041 | 28.315
|  | Floor | 2.2712 | 3.85 | 69.514 | 71.1 | 129.67 | 82.372 | 69.514 | 82.372
|  |  | 7.893 | 3.77 | -52.236 | 155.87 | 126.67 | -18.734 | 52.236 | 18.734
|  | Ceiling | 4.7187 | 4.63 | -1.8794 | 137.87 | 153 | 10.977 | 1.8794 | 10.977
[6 empty] | 221.16 | 152 | -31.272 |  | 31.272
| Test 13 | Long Wall |  |  |  | 110.38 | 195 | 76.662 |  | 76.662
[6 empty] | 199.2 | 198 | -0.60243 |  | 0.60243
|  | Short Wall |  |  |  | 126.8 | 194 | 52.997 |  | 52.997
[6 empty] | 144.6 | 195 | 34.855 |  | 34.855
|  | Floor |  |  |  | 89.58 | 166 | 85.308 |  | 85.308
[6 empty] | 148.3 | 161 | 8.5637 |  | 8.5637
|  | Ceiling |  |  |  | 319.03 | 196 | -38.563 |  | 38.563
[6 empty] | 497.44 | 197 | -60.397 |  | 60.397
| Test 16 | Long Wall |  |  |  | 107.3 | 175.17 | 63.249 |  | 63.249
[6 empty] | 217.06 | 180.17 | -16.997 |  | 16.997
|  | Short Wall |  |  |  | 123 | 175 | 42.276 |  | 42.276
[6 empty] | 141.1 | 176 | 24.734 |  | 24.734
|  | Floor |  |  |  | 79.992 | 148.17 | 85.226 |  | 85.226
[6 empty] | 145.5 | 144 | -1.0309 |  | 1.0309
|  | Ceiling |  |  |  | 283.2 | 178 | -37.147 |  | 37.147
[6 empty] | 441.44 | 180 | -59.225 |  | 59.225
| Test 17 | Long Wall | 1.4667 | 2.16 | 47.268 | 39 | 52.9 | 35.641 | 47.268 | 35.641
|  |  | 0.9286 | 2.36 | 154.15 | 82 | 65.2 | -20.488 | 154.15 | 20.488
|  | Short Wall | 1.5629 | 2.15 | 37.562 | 56.363 | 51.6 | -8.4502 | 37.562 | 8.4502
|  |  | 1.8988 | 2.16 | 13.755 | 60.965 | 54.017 | -11.397 | 13.755 | 11.397
|  | Floor | 0.85669 | 1.4 | 63.42 | 24.4 | 34.1 | 39.754 | 63.42 | 39.754
|  |  | 1.4977 | 1.35 | -9.8623 | 51.9 | 32.5 | -37.38 | 9.8623 | 37.38
|  | Ceiling |  |  |  | 68.673 | 57.717 | -15.954 |  | 15.954
[6 empty] | 229.76 | 64.3 | -72.015 |  | 72.015
| Test 3 | Long Wall | 3.4952 | 4.83 | 38.188 | 114.6 | 187 | 63.176 | 38.188 | 63.176
|  |  | 4.3188 | 5.32 | 23.183 | 172 | 203 | 18.023 | 23.183 | 18.023
|  | Short Wall | 2.5274 | 3.48 | 37.691 | 86.9 | 152 | 74.914 | 37.691 | 74.914
|  |  | 4.4423 | 4.94 | 11.204 | 145.6 | 191 | 31.181 | 11.204 | 31.181
|  | Floor | 1.9674 | 3.58 | 81.963 | 53.6 | 143 | 166.79 | 81.963 | 166.79
|  |  | 4.0486 | 3.46 | -14.538 | 118.3 | 139 | 17.498 | 14.538 | 17.498
|  | Ceiling | 4.5867 | 5.43 | 18.387 | 155.33 | 194 | 24.893 | 18.387 | 24.893
|  |  | 9.7624 | 5.54 | -43.252 | 287.1 | 197 | -31.383 | 43.252 | 31.383
| Test 9 | Long Wall | 3.4167 | 4.68 | 36.974 | 112.9 | 184 | 62.976 | 36.974 | 62.976
|  |  | 4.2022 | 5.17 | 23.031 | 177.73 | 200 | 12.528 | 23.031 | 12.528
|  | Short Wall | 2.3913 | 3.34 | 39.674 | 87.933 | 148 | 68.309 | 39.674 | 68.309
[6 empty] | 134.73 | 188 | 39.535 |  | 39.535
|  | Floor | 1.9126 | 3.43 | 79.334 | 53.083 | 139 | 161.85 | 79.334 | 161.85
|  |  | 3.8607 | 3.31 | -14.263 | 121.8 | 135 | 10.837 | 14.263 | 10.837
|  | Ceiling | 5.453 | 5.27 | -3.3559 | 203.6 | 191 | -6.1886 | 3.3559 | 6.1886
|  |  | 9.403 | 5.39 | -42.678 | 289.9 | 194 | -33.08 | 42.678 | 33.08
| Test 5 | Long Wall | 2.6754 | 3.46 | 29.326 | 93.7 | 146 | 55.816 | 29.326 | 55.816
|  |  | 3.8164 | 4.06 | 6.383 | 154.4 | 168 | 8.8083 | 6.383 | 8.8083
|  | Short Wall | 1.9808 | 2.48 | 25.204 | 71.117 | 116 | 63.112 | 25.204 | 63.112
|  |  | 3.2916 | 3.51 | 6.6353 | 117.5 | 148 | 25.957 | 6.6353 | 25.957
|  | Floor | 1.3953 | 2.48 | 77.735 | 41.6 | 107 | 157.21 | 77.735 | 157.21
|  |  | 10.011 | 2.41 | -75.927 | 171 | 104 | -39.181 | 75.927 | 39.181
|  | Ceiling | 3.3587 | 3.9 | 16.115 | 124.9 | 151 | 20.897 | 16.115 | 20.897
|  |  | 6.7404 | 4.11 | -39.024 | 263.2 | 159 | -39.59 | 39.024 | 39.59
| Test 14 | Long Wall | 3.4901 | 4.7 | 34.668 | 114.4 | 184 | 60.839 | 34.668 | 60.839
|  |  | 8.1 | 5.9 | -27.16 | 254.37 | 222 | -12.724 | 27.16 | 12.724
|  | Short Wall | 2.3421 | 3.4 | 45.169 | 86.8 | 149 | 71.659 | 45.169 | 71.659
|  |  | 4.4688 | 4.84 | 8.3066 | 147.6 | 189 | 28.049 | 8.3066 | 28.049
|  | Floor | 1.8899 | 3.49 | 84.666 | 52.2 | 141 | 170.11 | 84.666 | 170.11
|  |  | 2.9711 | 3.37 | 13.426 | 103.8 | 137 | 31.985 | 13.426 | 31.985
|  | Ceiling | 4.683 | 5.33 | 13.816 | 157.7 | 192 | 21.75 | 13.816 | 21.75
|  |  | 8.9956 | 5.6 | -37.747 | 350.63 | 200 | -42.96 | 37.747 | 42.96
| Test 15 | Long Wall | 3.6362 | 4.54 | 24.856 | 219.2 | 183 | -16.515 | 24.856 | 16.515
|  |  | 7.4526 | 4.67 | -37.337 | 205.2 | 188 | -8.382 | 37.337 | 8.382
|  | Short Wall | 2.5828 | 3.2 | 23.896 | 95.8 | 145 | 51.357 | 23.896 | 51.357
|  |  | 4.6511 | 4.66 | 0.19215 | 151 | 187 | 23.841 | 0.19215 | 23.841
|  | Floor | 1.9428 | 3.26 | 67.8 | 52.233 | 137 | 162.28 | 67.8 | 162.28
|  |  | 5.1714 | 3.15 | -39.088 | 131.1 | 132 | 0.68666 | 39.088 | 0.68666
|  | Ceiling |  |  |  | 157 | 191 | 21.656 |  | 21.656
[6 empty] | 287.1 | 186 | -35.214 |  | 35.214
| Test 18 | Long Wall | 3.3999 | 4.68 | 37.651 | 118.1 | 185 | 56.647 | 37.651 | 56.647
[6 empty] | 312.53 | 248 | -20.648 |  | 20.648
|  | Short Wall | 2.5491 | 3.43 | 34.558 | 93.8 | 154 | 64.179 | 34.558 | 64.179
|  |  | 4.6567 | 4.88 | 4.7959 | 152.6 | 190 | 24.509 | 4.7959 | 24.509
|  | Floor | 1.7892 | 3.5 | 95.622 | 49.533 | 141 | 184.66 | 95.622 | 184.66
|  |  | 3.0577 | 3.38 | 10.542 | 106.2 | 137 | 29.002 | 10.542 | 29.002
|  | Ceiling | 4.4763 | 5.35 | 19.518 | 144.6 | 193 | 33.472 | 19.518 | 33.472
[6 empty] | 249.63 | 194 | -22.286 |  | 22.286
iBMB Pool | Test 1 | M 19 |  |  |  | 595.8 | 569 | -4.4981 |  | 4.4981
|  | M 20 |  |  |  | 723.2 | 261 | -63.91 |  | 63.91
iBMB Cable | Test 4 | TW 1-1 |  |  |  | 56.2 | 39.9 | -29.004 |  | 29.004
|  | TW 2-1 |  |  |  | 4.5 | 27 | 500 |  | 500
|  | TW 1-4 |  |  |  | 87.1 | 39.1 | -55.109 |  | 55.109
|  | TW 2-4 |  |  |  | 67.967 | 37.6 | -44.679 |  | 44.679
|  | TW 1-7 |  |  |  | 86.033 | 39.5 | -54.088 |  | 54.088
|  | TW 2-7 |  |  |  | 72 | 39.2 | -45.556 |  | 45.556
Average ----> |  |  |  |  | 16.2229 |  |  | 25.1428 | 35.0388 | 46.1367
Standard Deviation ----> |  |  |  |  | 41.2646 |  |  | 66.4401 | 26.981 | 53.9079
Median ----> |  |  |  |  | 16.115 |  |  | 21.703 | 30.529 | 35.0345
Percentile ranking at uncertainty limit ----> | [8 empty] | 0.34 | 0.174
90th percentile value ----> | [8 empty] | 73.3618 | 75.892