## Sheet1
you can edit quantities in bold - non-bold items are computed by spreadsheet. CFAST temperature and pressure (in bold) are copied from a CFAST run
dx | dy | dz | qfire | lamr | gamma | cp | cv | Rgas | P0 | T0 | rho0 | M0 | E0
5 | 5 | 5 | 100000 | 0 | 1.4 | 1012 | 722.8571 | 289.1429 | 101300 | 293.15 | 1.1951 | 149.3735 | 31653084.375
Volume |  |  | qrad | qconv | hcomb | mfire
124.9875 |  |  | 0 | 100000 | 50000 | 0.002
(Note volume calculated in CFAST is (1-1e-4)*Actual_volume to allow for a non-disappearing second layer (pressure calculation though uses full compartment volume)
|  | calculated pressure |  | calc temperature |  | cfast temperature |  |  |  | cfast pressure |  |  |  | Formulas (assuming constant fire)
Time | E | DP | M | T=E/(CV*M)-273.15 |  | temperature | abs error | rel error % |  | DP | abs error | rel error %
0 | 31653084.375 | 0 | 149.3735 | 20 |  | 20 | 0 | 0 |  | 0 | 0 | 0 |  | DP=(gamma-1)*qtotal*Time/Volume
10 | 32659017.731 | 3200 | 149.3935 | 29.2758 |  | 29.2764 | 0.00060098 | 0.00019872 |  | 3219.29 | 19.29 | 0.018459 |  | M=M0+mfire*Time
20 | 33665326.5713 | 6400 | 149.4135 | 38.5526 |  | 38.5521 | -0.00049135 | -0.00015763 |  | 6439.18 | 39.18 | 0.036379 |  | E=E0+qconvec*Time+(M-M0)*cp*T (note actually we use T_i-1 to allow an analytical solution)
30 | 34672010.9563 | 9600 | 149.4335 | 47.8304 |  | 47.8271 | -0.0032771 | -0.001021 |  | 9659.66 | 59.66 | 0.053796 |  | T=E/(cv*M)-273.15
40 | 35679070.9463 | 12800 | 149.4535 | 57.1092 |  | 57.1013 | -0.0078565 | -0.0023789 |  | 12880.8 | 80.8 | 0.070815
50 | 36686506.6016 | 16000 | 149.4735 | 66.3889 |  | 66.3748 | -0.01413 | -0.0041614 |  | 16102.4 | 102.4 | 0.087298
60 | 37694317.9826 | 19200 | 149.4935 | 75.6697 |  | 75.6476 | -0.022097 | -0.0063347 |  | 19324.7 | 124.7 | 0.10349
70 | 38702505.1497 | 22400 | 149.5135 | 84.9515 |  | 84.9197 | -0.031758 | -0.0088685 |  | 22547.6 | 147.6 | 0.11932
80 | 39711068.1631 | 25600 | 149.5335 | 94.2342 |  | 94.191 | -0.043214 | -0.011763 |  | 25771.1 | 171.1 | 0.13483
90 | 40720007.0833 | 28800 | 149.5535 | 103.518 |  | 103.462 | -0.055963 | -0.014858 |  | 28995.2 | 195.2 | 0.15004
100 | 41729321.9708 | 32000 | 149.5735 | 112.8027 |  | 112.731 | -0.071708 | -0.018579 |  | 32219.9 | 219.9 | 0.16497
110 | 42739012.8859 | 35200 | 149.5935 | 122.0884 |  | 122.001 | -0.087447 | -0.022125 |  | 35445.2 | 245.2 | 0.17963
120 | 43749079.8891 | 38400 | 149.6135 | 131.3752 |  | 131.269 | -0.10618 | -0.026248 |  | 38671.1 | 271.1 | 0.19406
130 | 44759523.0407 | 41600 | 149.6335 | 140.6629 |  | 140.537 | -0.12591 | -0.030427 |  | 41897.6 | 297.6 | 0.20826
140 | 45770342.4013 | 44800 | 149.6535 | 149.9516 |  | 149.804 | -0.14763 | -0.034893 |  | 45124.7 | 324.7 | 0.22225
150 | 46781538.0314 | 48000 | 149.6735 | 159.2414 |  | 159.07 | -0.17135 | -0.03963 |  | 48352.4 | 352.4 | 0.23603
160 | 47793109.9913 | 51200 | 149.6935 | 168.5321 |  | 168.335 | -0.19707 | -0.044618 |  | 51580.7 | 380.7 | 0.24964
170 | 48805058.3416 | 54400 | 149.7135 | 177.8238 |  | 177.6 | -0.22378 | -0.049622 |  | 54809.6 | 409.6 | 0.26307
180 | 49817383.1429 | 57600 | 149.7335 | 187.1165 |  | 186.864 | -0.25249 | -0.054857 |  | 58039.1 | 439.1 | 0.27634
190 | 50830084.4556 | 60800 | 149.7535 | 196.4102 |  | 196.128 | -0.28219 | -0.060097 |  | 61269.1 | 469.1 | 0.28939
200 | 51843162.3402 | 64000 | 149.7735 | 205.7049 |  | 205.39 | -0.31489 | -0.065759 |  | 64499.8 | 499.8 | 0.30236
210 | 52856616.8574 | 67200 | 149.7935 | 215.0006 |  | 214.652 | -0.34859 | -0.071409 |  | 67731.1 | 531.1 | 0.31519
220 | 53870448.0676 | 70400 | 149.8135 | 224.2973 |  | 223.913 | -0.38428 | -0.07725 |  | 70963 | 563 | 0.3279
230 | 54884656.0315 | 73600 | 149.8335 | 233.595 |  | 233.174 | -0.42097 | -0.083073 |  | 74195.5 | 595.5 | 0.34048
240 | 55899240.8096 | 76800 | 149.8535 | 242.8937 |  | 242.433 | -0.46065 | -0.089266 |  | 77428.6 | 628.6 | 0.35295
250 | 56914202.4625 | 80000 | 149.8735 | 252.1933 |  | 251.692 | -0.50133 | -0.09543 |  | 80662.3 | 662.3 | 0.36531
260 | 57929541.0508 | 83200 | 149.8935 | 261.494 |  | 260.95 | -0.54401 | -0.10175 |  | 83896.6 | 696.6 | 0.37756
270 | 58945256.6353 | 86400 | 149.9135 | 270.7957 |  | 270.208 | -0.58769 | -0.10804 |  | 87131.5 | 731.5 | 0.38972
280 | 59961349.2764 | 89600 | 149.9335 | 280.0984 |  | 279.465 | -0.63336 | -0.11448 |  | 90367 | 767 | 0.40178
290 | 60977819.0348 | 92800 | 149.9535 | 289.402 |  | 288.721 | -0.68104 | -0.12106 |  | 93603.1 | 803.1 | 0.41376
300 | 61994665.9713 | 96000 | 149.9735 | 298.7067 |  | 297.976 | -0.73071 | -0.12778 |  | 96839.8 | 839.8 | 0.42565
310 | 63011890.1464 | 99200 | 149.9935 | 308.0124 |  | 307.231 | -0.78137 | -0.13445 |  | 100077 | 877 | 0.43741
320 | 64029491.621 | 102400 | 150.0135 | 317.319 |  | 316.484 | -0.83504 | -0.14142 |  | 103315 | 915 | 0.44919
330 | 65047470.4556 | 105600 | 150.0335 | 326.6267 |  | 325.737 | -0.8897 | -0.14834 |  | 106553 | 953 | 0.46061
340 | 66065826.711 | 108800 | 150.0535 | 335.9354 |  | 334.99 | -0.94537 | -0.15521 |  | 109793 | 993 | 0.47263
350 | 67084560.4479 | 112000 | 150.0735 | 345.245 |  | 344.241 | -1.004 | -0.16236 |  | 113032 | 1032 | 0.48383
360 | 68103671.7271 | 115200 | 150.0935 | 354.5557 |  | 353.492 | -1.0637 | -0.16946 |  | 116272 | 1072 | 0.49515
370 | 69123160.6093 | 118400 | 150.1135 | 363.8673 |  | 362.743 | -1.1243 | -0.1765 |  | 119513 | 1113 | 0.5066
380 | 70143027.1553 | 121600 | 150.1335 | 373.18 |  | 371.992 | -1.188 | -0.18381 |  | 122755 | 1155 | 0.51817
390 | 71163271.4258 | 124800 | 150.1535 | 382.4937 |  | 381.241 | -1.2527 | -0.19106 |  | 125997 | 1197 | 0.52941
400 | 72183893.4817 | 128000 | 150.1735 | 391.8083 |  | 390.489 | -1.3193 | -0.19841 |  | 129240 | 1240 | 0.54078
410 | 73204893.3838 | 131200 | 150.1935 | 401.124 |  | 399.736 | -1.388 | -0.20585 |  | 132483 | 1283 | 0.55183
420 | 74226271.1929 | 134400 | 150.2135 | 410.4406 |  | 408.983 | -1.4576 | -0.21323 |  | 135727 | 1327 | 0.563
430 | 75248026.9697 | 137600 | 150.2335 | 419.7583 |  | 418.228 | -1.5303 | -0.22085 |  | 138971 | 1371 | 0.57388
440 | 76270160.7753 | 140800 | 150.2535 | 429.0769 |  | 427.473 | -1.6039 | -0.22841 |  | 142216 | 1416 | 0.58488
450 | 77292672.6704 | 144000 | 150.2735 | 438.3966 |  | 436.718 | -1.6786 | -0.23591 |  | 145462 | 1462 | 0.596
460 | 78315562.7158 | 147200 | 150.2935 | 447.7172 |  | 445.961 | -1.7562 | -0.24363 |  | 148708 | 1508 | 0.60684
470 | 79338830.9726 | 150400 | 150.3135 | 457.0389 |  | 455.204 | -1.8349 | -0.25129 |  | 151955 | 1555 | 0.6178
480 | 80362477.5015 | 153600 | 150.3335 | 466.3616 |  | 464.446 | -1.9156 | -0.25903 |  | 155203 | 1603 | 0.62887
490 | 81386502.3635 | 156800 | 150.3535 | 475.6852 |  | 473.688 | -1.9972 | -0.26671 |  | 158451 | 1651 | 0.63967
500 | 82410905.6195 | 160000 | 150.3735 | 485.0099 |  | 482.929 | -2.0809 | -0.27446 |  | 161699 | 1699 | 0.65021
510 | 83435687.3305 | 163200 | 150.3935 | 494.3355 |  | 492.169 | -2.1665 | -0.28229 |  | 164949 | 1749 | 0.66125
520 | 84460847.5573 | 166400 | 150.4135 | 503.6622 |  | 501.408 | -2.2542 | -0.29019 |  | 168199 | 1799 | 0.67202
530 | 85486386.361 | 169600 | 150.4335 | 512.9899 |  | 510.646 | -2.3439 | -0.29815 |  | 171449 | 1849 | 0.68254
540 | 86512303.8026 | 172800 | 150.4535 | 522.3185 |  | 519.884 | -2.4345 | -0.30605 |  | 174700 | 1900 | 0.69318
550 | 87538599.943 | 176000 | 150.4735 | 531.6482 |  | 529.121 | -2.5272 | -0.31402 |  | 177952 | 1952 | 0.70393
560 | 88565274.8432 | 179200 | 150.4935 | 540.9789 |  | 538.358 | -2.6209 | -0.32192 |  | 181204 | 2004 | 0.71444
570 | 89592328.5643 | 182400 | 150.5135 | 550.3105 |  | 547.593 | -2.7175 | -0.33001 |  | 184457 | 2057 | 0.72506
580 | 90619761.1672 | 185600 | 150.5335 | 559.6432 |  | 556.828 | -2.8152 | -0.33804 |  | 187710 | 2110 | 0.73545
590 | 91647572.7131 | 188800 | 150.5535 | 568.9769 |  | 566.062 | -2.9149 | -0.34613 |  | 190964 | 2164 | 0.74595
600 | 92675763.2629 | 192000 | 150.5735 | 578.3116 |  | 575.296 | -3.0156 | -0.35416 |  | 194219 | 2219 | 0.75656
610 | 93704332.8778 | 195200 | 150.5935 | 587.6472 |  | 584.528 | -3.1192 | -0.36237 |  | 197474 | 2274 | 0.76695
620 | 94733281.6188 | 198400 | 150.6135 | 596.9839 |  | 593.76 | -3.2239 | -0.37051 |  | 200730 | 2330 | 0.77744
630 | 95762609.547 | 201600 | 150.6335 | 606.3216 |  | 602.991 | -3.3306 | -0.37871 |  | 203987 | 2387 | 0.78805
640 | 96792316.7236 | 204800 | 150.6535 | 615.6603 |  | 612.222 | -3.4383 | -0.38684 |  | 207244 | 2444 | 0.79843
650 | 97822403.2096 | 208000 | 150.6735 | 625 |  | 621.452 | -3.548 | -0.39503 |  | 210501 | 2501 | 0.8086
660 | 98852869.0661 | 211200 | 150.6935 | 634.3407 |  | 630.681 | -3.6597 | -0.40328 |  | 213759 | 2559 | 0.81888
670 | 99883714.3544 | 214400 | 150.7135 | 643.6824 |  | 639.909 | -3.7734 | -0.41157 |  | 217018 | 2618 | 0.82927
680 | 100914939.1356 | 217600 | 150.7335 | 653.0251 |  | 649.137 | -3.8881 | -0.4198 |  | 220278 | 2678 | 0.83976
690 | 101946543.4708 | 220800 | 150.7535 | 662.3688 |  | 658.363 | -4.0058 | -0.42819 |  | 223538 | 2738 | 0.85005
700 | 102978527.4213 | 224000 | 150.7735 | 671.7135 |  | 667.59 | -4.1235 | -0.43641 |  | 226798 | 2798 | 0.86013
710 | 104010891.0482 | 227200 | 150.7935 | 681.0592 |  | 676.815 | -4.2442 | -0.44479 |  | 230060 | 2860 | 0.87062
720 | 105043634.4128 | 230400 | 150.8135 | 690.406 |  | 686.04 | -4.366 | -0.45311 |  | 233321 | 2921 | 0.88062
730 | 106076757.5763 | 233600 | 150.8335 | 699.7537 |  | 695.264 | -4.4897 | -0.46147 |  | 236584 | 2984 | 0.89101
740 | 107110260.5999 | 236800 | 150.8535 | 709.1024 |  | 704.487 | -4.6154 | -0.46988 |  | 239847 | 3047 | 0.90121
750 | 108144143.5448 | 240000 | 150.8735 | 718.4522 |  | 713.709 | -4.7432 | -0.47833 |  | 243111 | 3111 | 0.91151
760 | 109178406.4724 | 243200 | 150.8935 | 727.8029 |  | 722.931 | -4.8719 | -0.48673 |  | 246375 | 3175 | 0.92163
770 | 110213049.444 | 246400 | 150.9135 | 737.1546 |  | 732.152 | -5.0026 | -0.49516 |  | 249640 | 3240 | 0.93184
780 | 111248072.5207 | 249600 | 150.9335 | 746.5074 |  | 741.372 | -5.1354 | -0.50364 |  | 252905 | 3305 | 0.94186
790 | 112283475.7639 | 252800 | 150.9535 | 755.8612 |  | 750.592 | -5.2692 | -0.51206 |  | 256171 | 3371 | 0.95199
800 | 113319259.235 | 256000 | 150.9735 | 765.2159 |  | 759.811 | -5.4049 | -0.52052 |  | 259438 | 3438 | 0.96222
810 | 114355422.9952 | 259200 | 150.9935 | 774.5717 |  | 769.029 | -5.5427 | -0.52902 |  | 262705 | 3505 | 0.97226
820 | 115391967.106 | 262400 | 151.0135 | 783.9285 |  | 778.246 | -5.6825 | -0.53756 |  | 265973 | 3573 | 0.9824
830 | 116428891.6286 | 265600 | 151.0335 | 793.2862 |  | 787.463 | -5.8232 | -0.54605 |  | 269241 | 3641 | 0.99237
840 | 117466196.6245 | 268800 | 151.0535 | 802.645 |  | 796.679 | -5.966 | -0.55457 |  | 272510 | 3710 | 1.0024
850 | 118503882.1549 | 272000 | 151.0735 | 812.0048 |  | 805.894 | -6.1108 | -0.56313 |  | 275780 | 3780 | 1.0126
860 | 119541948.2814 | 275200 | 151.0935 | 821.3656 |  | 815.109 | -6.2566 | -0.57163 |  | 279050 | 3850 | 1.0226
870 | 120580395.0653 | 278400 | 151.1135 | 830.7274 |  | 824.322 | -6.4054 | -0.58027 |  | 282321 | 3921 | 1.0327
880 | 121619222.5681 | 281600 | 151.1335 | 840.0903 |  | 833.535 | -6.5553 | -0.58885 |  | 285592 | 3992 | 1.0426
890 | 122658430.8511 | 284800 | 151.1535 | 849.4541 |  | 842.748 | -6.7061 | -0.59737 |  | 288864 | 4064 | 1.0526
900 | 123698019.9759 | 288000 | 151.1735 | 858.8189 |  | 851.959 | -6.8599 | -0.60602 |  | 292136 | 4136 | 1.0624

## Sheet2
Time | ULT
0 | 20
10 | 29.2758
20 | 38.5526
30 | 47.8304
40 | 57.1092
50 | 66.3889
60 | 75.6697
70 | 84.9515
80 | 94.2342
90 | 103.518
100 | 112.8027
110 | 122.0884
120 | 131.3752
130 | 140.6629
140 | 149.9516
150 | 159.2414
160 | 168.5321
170 | 177.8238
180 | 187.1165
190 | 196.4102
200 | 205.7049
210 | 215.0006
220 | 224.2973
230 | 233.595
240 | 242.8937
250 | 252.1933
260 | 261.494
270 | 270.7957
280 | 280.0984
290 | 289.402
300 | 298.7067
310 | 308.0124
320 | 317.319
330 | 326.6267
340 | 335.9354
350 | 345.245
360 | 354.5557
370 | 363.8673
380 | 373.18
390 | 382.4937
400 | 391.8083
410 | 401.124
420 | 410.4406
430 | 419.7583
440 | 429.0769
450 | 438.3966
460 | 447.7172
470 | 457.0389
480 | 466.3616
490 | 475.6852
500 | 485.0099
510 | 494.3355
520 | 503.6622
530 | 512.9899
540 | 522.3185
550 | 531.6482
560 | 540.9789
570 | 550.3105
580 | 559.6432
590 | 568.9769
600 | 578.3116
610 | 587.6472
620 | 596.9839
630 | 606.3216
640 | 615.6603
650 | 625
660 | 634.3407
670 | 643.6824
680 | 653.0251
690 | 662.3688
700 | 671.7135
710 | 681.0592
720 | 690.406
730 | 699.7537
740 | 709.1024
750 | 718.4522
760 | 727.8029
770 | 737.1546
780 | 746.5074
790 | 755.8612
800 | 765.2159
810 | 774.5717
820 | 783.9285
830 | 793.2862
840 | 802.645
850 | 812.0048
860 | 821.3656
870 | 830.7274
880 | 840.0903
890 | 849.4541
900 | 858.8189