## Sheet1
you can edit quantities in bold - non-bold items are computed by spreadsheet. CFAST temperature and pressure (in bold) are copied from a CFAST run
dx | dy | dz | qfire | lamr | gamma | cp | cv | Rgas | P0 | T0 | rho0 | M0 | E0
5 | 5 | 5 | 100000 | 0 | 1.4 | 1012 | 722.8571 | 289.1429 | 101300 | 293.15 | 1.1951 | 149.3735 | 31653084.375
Volume |  |  | qrad | qconv | hcomb | mfire
124.9875 |  |  | 0 | 100000 | 50000 | 0.002
(Note volume calculated in CFAST is (1-1e-4)*Actual_volume to allow for a non-disappearing second layer (pressure calculation though uses full compartment volume)
|  | calculated pressure |  | calc temperature |  | cfast temperature |  |  |  | cfast pressure |  |  |  | Formulas (assuming constant fire)
Time | E | DP | M | T=E/(CV*M)-273.15 |  | temperature | abs error | rel error % |  | DP | abs error | rel error %
0 | 31653084.375 | 0 | 149.3735 | 20 |  | 20 | 0 | 0 |  | 0 | 0 | 0 |  | DP=(gamma-1)*qtotal*Time/Volume
10 | 32659017.731 | 3200 | 149.3935 | 29.2758 |  | 21.1596 | -8.1162 | -2.6837 |  | 402.378 | -2797.622 | -2.6772 |  | M=M0+mfire*Time
20 | 33665326.5713 | 6400 | 149.4135 | 38.5526 |  | 22.3192 | -16.2334 | -5.208 |  | 804.765 | -5595.235 | -5.1952 |  | E=E0+qconvec*Time+(M-M0)*cp*T (note actually we use T_i-1 to allow an analytical solution)
30 | 34672010.9563 | 9600 | 149.4335 | 47.8304 |  | 23.4787 | -24.3517 | -7.5867 |  | 1207.16 | -8392.84 | -7.5679 |  | T=E/(cv*M)-273.15
40 | 35679070.9463 | 12800 | 149.4535 | 57.1092 |  | 24.6383 | -32.4709 | -9.8319 |  | 1609.57 | -11190.43 | -9.8076
50 | 36686506.6016 | 16000 | 149.4735 | 66.3889 |  | 25.7978 | -40.5911 | -11.9548 |  | 2011.98 | -13988.02 | -11.925
60 | 37694317.9826 | 19200 | 149.4935 | 75.6697 |  | 26.9574 | -48.7123 | -13.9649 |  | 2414.41 | -16785.59 | -13.93
70 | 38702505.1497 | 22400 | 149.5135 | 84.9515 |  | 28.1169 | -56.8346 | -15.8711 |  | 2816.84 | -19583.16 | -15.8312
80 | 39711068.1631 | 25600 | 149.5335 | 94.2342 |  | 29.2764 | -64.9578 | -17.6812 |  | 3219.29 | -22380.71 | -17.6365
90 | 40720007.0833 | 28800 | 149.5535 | 103.518 |  | 30.4359 | -73.0821 | -19.4023 |  | 3621.74 | -25178.26 | -19.353
100 | 41729321.9708 | 32000 | 149.5735 | 112.8027 |  | 31.5954 | -81.2073 | -21.0407 |  | 4024.2 | -27975.8 | -20.9871
110 | 42739012.8859 | 35200 | 149.5935 | 122.0884 |  | 32.7549 | -89.3335 | -22.6024 |  | 4426.67 | -30773.33 | -22.5446
120 | 43749079.8891 | 38400 | 149.6135 | 131.3752 |  | 33.9143 | -97.4609 | -24.0927 |  | 4829.16 | -33570.84 | -24.0307
130 | 44759523.0407 | 41600 | 149.6335 | 140.6629 |  | 35.0738 | -105.5891 | -25.5161 |  | 5231.65 | -36368.35 | -25.4502
140 | 45770342.4013 | 44800 | 149.6535 | 149.9516 |  | 36.2332 | -113.7184 | -26.8773 |  | 5634.15 | -39165.85 | -26.8076
150 | 46781538.0314 | 48000 | 149.6735 | 159.2414 |  | 37.3927 | -121.8487 | -28.1802 |  | 6036.66 | -41963.34 | -28.1067
160 | 47793109.9913 | 51200 | 149.6935 | 168.5321 |  | 38.5521 | -129.98 | -29.4284 |  | 6439.18 | -44760.82 | -29.3514
170 | 48805058.3416 | 54400 | 149.7135 | 177.8238 |  | 39.7115 | -138.1123 | -30.6253 |  | 6841.7 | -47558.3 | -30.5448
180 | 49817383.1429 | 57600 | 149.7335 | 187.1165 |  | 40.8709 | -146.2456 | -31.7741 |  | 7244.24 | -50355.76 | -31.6902
190 | 50830084.4556 | 60800 | 149.7535 | 196.4102 |  | 42.0303 | -154.3799 | -32.8776 |  | 7646.79 | -53153.21 | -32.7904
200 | 51843162.3402 | 64000 | 149.7735 | 205.7049 |  | 43.1897 | -162.5152 | -33.9383 |  | 8049.34 | -55950.66 | -33.8479
210 | 52856616.8574 | 67200 | 149.7935 | 215.0006 |  | 44.349 | -170.6516 | -34.9588 |  | 8451.91 | -58748.09 | -34.8653
220 | 53870448.0676 | 70400 | 149.8135 | 224.2973 |  | 45.5084 | -178.7889 | -35.9413 |  | 8854.49 | -61545.51 | -35.8448
230 | 54884656.0315 | 73600 | 149.8335 | 233.595 |  | 46.6677 | -186.9273 | -36.8878 |  | 9257.07 | -64342.93 | -36.7884
240 | 55899240.8096 | 76800 | 149.8535 | 242.8937 |  | 47.8271 | -195.0666 | -37.8004 |  | 9659.66 | -67140.34 | -37.6981
250 | 56914202.4625 | 80000 | 149.8735 | 252.1933 |  | 48.9864 | -203.2069 | -38.6808 |  | 10062.3 | -69937.7 | -38.5757
260 | 57929541.0508 | 83200 | 149.8935 | 261.494 |  | 50.1457 | -211.3483 | -39.5307 |  | 10464.9 | -72735.1 | -39.4228
270 | 58945256.6353 | 86400 | 149.9135 | 270.7957 |  | 51.305 | -219.4907 | -40.3516 |  | 10867.5 | -75532.5 | -40.2411
280 | 59961349.2764 | 89600 | 149.9335 | 280.0984 |  | 52.4643 | -227.6341 | -41.145 |  | 11270.1 | -78329.9 | -41.0319
290 | 60977819.0348 | 92800 | 149.9535 | 289.402 |  | 53.6235 | -235.7785 | -41.9123 |  | 11672.8 | -81127.2 | -41.7966
300 | 61994665.9713 | 96000 | 149.9735 | 298.7067 |  | 54.7828 | -243.9239 | -42.6547 |  | 12075.4 | -83924.6 | -42.5365
310 | 63011890.1464 | 99200 | 149.9935 | 308.0124 |  | 55.9421 | -252.0703 | -43.3735 |  | 12478.1 | -86721.9 | -43.2528
320 | 64029491.621 | 102400 | 150.0135 | 317.319 |  | 57.1013 | -260.2177 | -44.0697 |  | 12880.8 | -89519.2 | -43.9466
330 | 65047470.4556 | 105600 | 150.0335 | 326.6267 |  | 58.2605 | -268.3662 | -44.7444 |  | 13283.4 | -92316.6 | -44.6189
340 | 66065826.711 | 108800 | 150.0535 | 335.9354 |  | 59.4197 | -276.5157 | -45.3985 |  | 13686.1 | -95113.9 | -45.2708
350 | 67084560.4479 | 112000 | 150.0735 | 345.245 |  | 60.579 | -284.666 | -46.033 |  | 14088.8 | -97911.2 | -45.903
360 | 68103671.7271 | 115200 | 150.0935 | 354.5557 |  | 61.7381 | -292.8176 | -46.6489 |  | 14491.5 | -100708.5 | -46.5166
370 | 69123160.6093 | 118400 | 150.1135 | 363.8673 |  | 62.8973 | -300.97 | -47.2468 |  | 14894.2 | -103505.8 | -47.1123
380 | 70143027.1553 | 121600 | 150.1335 | 373.18 |  | 64.0565 | -309.1235 | -47.8275 |  | 15297 | -106303 | -47.6909
390 | 71163271.4258 | 124800 | 150.1535 | 382.4937 |  | 65.2157 | -317.278 | -48.3918 |  | 15699.7 | -109100.3 | -48.2531
400 | 72183893.4817 | 128000 | 150.1735 | 391.8083 |  | 66.3748 | -325.4335 | -48.9404 |  | 16102.4 | -111897.6 | -48.7997
410 | 73204893.3838 | 131200 | 150.1935 | 401.124 |  | 67.5339 | -333.5901 | -49.474 |  | 16505.2 | -114694.8 | -49.3311
420 | 74226271.1929 | 134400 | 150.2135 | 410.4406 |  | 68.6931 | -341.7475 | -49.993 |  | 16908 | -117492 | -49.8481
430 | 75248026.9697 | 137600 | 150.2335 | 419.7583 |  | 69.8522 | -349.9061 | -50.4982 |  | 17310.7 | -120289.3 | -50.3513
440 | 76270160.7753 | 140800 | 150.2535 | 429.0769 |  | 71.0113 | -358.0656 | -50.99 |  | 17713.5 | -123086.5 | -50.8412
450 | 77292672.6704 | 144000 | 150.2735 | 438.3966 |  | 72.1704 | -366.2262 | -51.469 |  | 18116.3 | -125883.7 | -51.3183
460 | 78315562.7158 | 147200 | 150.2935 | 447.7172 |  | 73.3295 | -374.3877 | -51.9357 |  | 18519.1 | -128680.9 | -51.7831
470 | 79338830.9726 | 150400 | 150.3135 | 457.0389 |  | 74.4885 | -382.5504 | -52.3906 |  | 18921.9 | -131478.1 | -52.236
480 | 80362477.5015 | 153600 | 150.3335 | 466.3616 |  | 75.6476 | -390.714 | -52.8341 |  | 19324.7 | -134275.3 | -52.6776
490 | 81386502.3635 | 156800 | 150.3535 | 475.6852 |  | 76.8066 | -398.8786 | -53.2665 |  | 19727.6 | -137072.4 | -53.1083
500 | 82410905.6195 | 160000 | 150.3735 | 485.0099 |  | 77.9657 | -407.0442 | -53.6884 |  | 20130.4 | -139869.6 | -53.5284
510 | 83435687.3305 | 163200 | 150.3935 | 494.3355 |  | 79.1247 | -415.2108 | -54.1002 |  | 20533.2 | -142666.8 | -53.9383
520 | 84460847.5573 | 166400 | 150.4135 | 503.6622 |  | 80.2837 | -423.3785 | -54.502 |  | 20936.1 | -145463.9 | -54.3384
530 | 85486386.361 | 169600 | 150.4335 | 512.9899 |  | 81.4427 | -431.5472 | -54.8945 |  | 21339 | -148261 | -54.7291
540 | 86512303.8026 | 172800 | 150.4535 | 522.3185 |  | 82.6017 | -439.7168 | -55.2777 |  | 21741.8 | -151058.2 | -55.1106
550 | 87538599.943 | 176000 | 150.4735 | 531.6482 |  | 83.7607 | -447.8875 | -55.6521 |  | 22144.7 | -153855.3 | -55.4833
560 | 88565274.8432 | 179200 | 150.4935 | 540.9789 |  | 84.9197 | -456.0592 | -56.0181 |  | 22547.6 | -156652.4 | -55.8476
570 | 89592328.5643 | 182400 | 150.5135 | 550.3105 |  | 86.0786 | -464.2319 | -56.3757 |  | 22950.5 | -159449.5 | -56.2036
580 | 90619761.1672 | 185600 | 150.5335 | 559.6432 |  | 87.2376 | -472.4056 | -56.7254 |  | 23353.4 | -162246.6 | -56.5516
590 | 91647572.7131 | 188800 | 150.5535 | 568.9769 |  | 88.3965 | -480.5804 | -57.0675 |  | 23756.4 | -165043.6 | -56.892
600 | 92675763.2629 | 192000 | 150.5735 | 578.3116 |  | 89.5554 | -488.7562 | -57.402 |  | 24159.3 | -167840.7 | -57.2249
610 | 93704332.8778 | 195200 | 150.5935 | 587.6472 |  | 90.7143 | -496.9329 | -57.7294 |  | 24562.2 | -170637.8 | -57.5507
620 | 94733281.6188 | 198400 | 150.6135 | 596.9839 |  | 91.8732 | -505.1107 | -58.0498 |  | 24965.2 | -173434.8 | -57.8695
630 | 95762609.547 | 201600 | 150.6335 | 606.3216 |  | 93.0321 | -513.2895 | -58.3634 |  | 25368.1 | -176231.9 | -58.1815
640 | 96792316.7236 | 204800 | 150.6535 | 615.6603 |  | 94.191 | -521.4693 | -58.6705 |  | 25771.1 | -179028.9 | -58.4871
650 | 97822403.2096 | 208000 | 150.6735 | 625 |  | 95.3499 | -529.6501 | -58.9712 |  | 26174.1 | -181825.9 | -58.7863
660 | 98852869.0661 | 211200 | 150.6935 | 634.3407 |  | 96.5087 | -537.832 | -59.2658 |  | 26577.1 | -184622.9 | -59.0793
670 | 99883714.3544 | 214400 | 150.7135 | 643.6824 |  | 97.6675 | -546.0149 | -59.5545 |  | 26980.1 | -187419.9 | -59.3665
680 | 100914939.1356 | 217600 | 150.7335 | 653.0251 |  | 98.8264 | -554.1987 | -59.8374 |  | 27383.1 | -190216.9 | -59.6478
690 | 101946543.4708 | 220800 | 150.7535 | 662.3688 |  | 99.9852 | -562.3836 | -60.1146 |  | 27786.1 | -193013.9 | -59.9236
700 | 102978527.4213 | 224000 | 150.7735 | 671.7135 |  | 101.144 | -570.5695 | -60.3864 |  | 28189.1 | -195810.9 | -60.1939
710 | 104010891.0482 | 227200 | 150.7935 | 681.0592 |  | 102.303 | -578.7562 | -60.653 |  | 28592.2 | -198607.8 | -60.459
720 | 105043634.4128 | 230400 | 150.8135 | 690.406 |  | 103.462 | -586.944 | -60.9144 |  | 28995.2 | -201404.8 | -60.719
730 | 106076757.5763 | 233600 | 150.8335 | 699.7537 |  | 104.62 | -595.1337 | -61.1709 |  | 29398.3 | -204201.7 | -60.9739
740 | 107110260.5999 | 236800 | 150.8535 | 709.1024 |  | 105.779 | -603.3234 | -61.4224 |  | 29801.3 | -206998.7 | -61.2241
750 | 108144143.5448 | 240000 | 150.8735 | 718.4522 |  | 106.938 | -611.5142 | -61.6693 |  | 30204.4 | -209795.6 | -61.4696
760 | 109178406.4724 | 243200 | 150.8935 | 727.8029 |  | 108.097 | -619.7059 | -61.9116 |  | 30607.5 | -212592.5 | -61.7104
770 | 110213049.444 | 246400 | 150.9135 | 737.1546 |  | 109.255 | -627.8996 | -62.1495 |  | 31010.6 | -215389.4 | -61.9469
780 | 111248072.5207 | 249600 | 150.9335 | 746.5074 |  | 110.414 | -636.0934 | -62.3831 |  | 31413.7 | -218186.3 | -62.1791
790 | 112283475.7639 | 252800 | 150.9535 | 755.8612 |  | 111.573 | -644.2882 | -62.6124 |  | 31816.8 | -220983.2 | -62.407
800 | 113319259.235 | 256000 | 150.9735 | 765.2159 |  | 112.731 | -652.4849 | -62.8377 |  | 32219.9 | -223780.1 | -62.6309
810 | 114355422.9952 | 259200 | 150.9935 | 774.5717 |  | 113.89 | -660.6817 | -63.0589 |  | 32623 | -226577 | -62.8508
820 | 115391967.106 | 262400 | 151.0135 | 783.9285 |  | 115.049 | -668.8795 | -63.2762 |  | 33026.2 | -229373.8 | -63.0668
830 | 116428891.6286 | 265600 | 151.0335 | 793.2862 |  | 116.207 | -677.0792 | -63.4899 |  | 33429.3 | -232170.7 | -63.279
840 | 117466196.6245 | 268800 | 151.0535 | 802.645 |  | 117.366 | -685.279 | -63.6998 |  | 33832.5 | -234967.5 | -63.4876
850 | 118503882.1549 | 272000 | 151.0735 | 812.0048 |  | 118.525 | -693.4798 | -63.9061 |  | 34235.6 | -237764.4 | -63.6926
860 | 119541948.2814 | 275200 | 151.0935 | 821.3656 |  | 119.683 | -701.6826 | -64.109 |  | 34638.8 | -240561.2 | -63.8941
870 | 120580395.0653 | 278400 | 151.1135 | 830.7274 |  | 120.842 | -709.8854 | -64.3084 |  | 35042 | -243358 | -64.0922
880 | 121619222.5681 | 281600 | 151.1335 | 840.0903 |  | 122.001 | -718.0893 | -64.5044 |  | 35445.2 | -246154.8 | -64.287
890 | 122658430.8511 | 284800 | 151.1535 | 849.4541 |  | 123.159 | -726.2951 | -64.6973 |  | 35848.4 | -248951.6 | -64.4785
900 | 123698019.9759 | 288000 | 151.1735 | 858.8189 |  | 124.318 | -734.5009 | -64.887 |  | 36251.6 | -251748.4 | -64.6669

## Sheet2
Time | ULT
0 | 20
10 | 29.2758
20 | 38.5526
30 | 47.8304
40 | 57.1092
50 | 66.3889
60 | 75.6697
70 | 84.9515
80 | 94.2342
90 | 103.518
100 | 112.8027
110 | 122.0884
120 | 131.3752
130 | 140.6629
140 | 149.9516
150 | 159.2414
160 | 168.5321
170 | 177.8238
180 | 187.1165
190 | 196.4102
200 | 205.7049
210 | 215.0006
220 | 224.2973
230 | 233.595
240 | 242.8937
250 | 252.1933
260 | 261.494
270 | 270.7957
280 | 280.0984
290 | 289.402
300 | 298.7067
310 | 308.0124
320 | 317.319
330 | 326.6267
340 | 335.9354
350 | 345.245
360 | 354.5557
370 | 363.8673
380 | 373.18
390 | 382.4937
400 | 391.8083
410 | 401.124
420 | 410.4406
430 | 419.7583
440 | 429.0769
450 | 438.3966
460 | 447.7172
470 | 457.0389
480 | 466.3616
490 | 475.6852
500 | 485.0099
510 | 494.3355
520 | 503.6622
530 | 512.9899
540 | 522.3185
550 | 531.6482
560 | 540.9789
570 | 550.3105
580 | 559.6432
590 | 568.9769
600 | 578.3116
610 | 587.6472
620 | 596.9839
630 | 606.3216
640 | 615.6603
650 | 625
660 | 634.3407
670 | 643.6824
680 | 653.0251
690 | 662.3688
700 | 671.7135
710 | 681.0592
720 | 690.406
730 | 699.7537
740 | 709.1024
750 | 718.4522
760 | 727.8029
770 | 737.1546
780 | 746.5074
790 | 755.8612
800 | 765.2159
810 | 774.5717
820 | 783.9285
830 | 793.2862
840 | 802.645
850 | 812.0048
860 | 821.3656
870 | 830.7274
880 | 840.0903
890 | 849.4541
900 | 858.8189